Caledonian Mining Cables

AS/NZS 2802:2000 Reeling & Trailing Cables

Type 441 (class 1) 3.3 to 22KV

» Applications .............................................................................................................

Type 441 Class 1 series cable has lower insulation and sheath radials than Class 2 cables, designed for many uses, suitable for trailing and also suitable for reeling applications, have one central pilot and a semiconductive cradle supporting and protecting the power cores, which makes these cables less likely to be damaged from crushing and squashing.

» Standards .................................................................................................................

AS/NZS 2802:2000

AS/NZS 1125

AS/NZS 3808

AS/NZS 5000.1

» Construction ............................................................................................................

Semiconductive PCP Filling And Covering Reinforcement

Stranded Tinned Copper Conductor Conductor Screen

EPR Insulation

Central Extensible Pilot Cradle Separator Insulation Screen  Earth Conductor

Extra-heavy Duty PCP Sheath

3×Conductors: Flexible stranded tinned annealed copper conductor.

Conductor Screen: Semiconductive compound (for cables having a voltage rating of 3.3/3.3kV and above).

Insulation: EPR.

Insulation Screen: Semiconductive elastomer.

Cradle Separator: Semiconductive PCP.

Overall Core Screen: Semiconductive PCP filling and covering.

3×Interstitial Earth Conductor: Semiconductive PCP covered flexible stranded tinned copper conductor.

1×Central Extensible Pilot: EPR covered flexible stranded tinned copper conductor.

www.caledonian-cables.co.uk  www.addison-cables.com	35

Caledonian Mining Cables

AS/NZS 2802:2000 Reeling & Trailing Cables

Textile Reinforcement: Open-weave braid reinforcement.

Sheath: Extra-heavy duty PCP sheath. Extra-heavy duty CPE/CSP sheath can be oﬀered upon request.

»  Dimensions and Weight ..........................................................................................

| Nominal Conductor Area | Strand Size | Insulation Thickness | Earth Conductor |  | Pilot Conductor |  | Thickness of Sheath |  | Nominal Overall Diameter | Nominal Weight |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
|  |  |  | Strand Size | Thickness of Covering | Strand Size | Thickness of Covering |  |  |  |  |
| mm² | No/mm | mm | No/mm | mm | No/mm | mm |  | mm | mm | kg/100m |
| Type 441.3 Class1 |  |  |  |  |  |  |  |  |  |  |
| 16 | 126/0.40 | 2.2 | 81/0.30 | 1.0 | 24/0.20 | 0.8 |  | 4.6 | 43.0 | 241 |
| 25 | 209/0.40 | 2.2 | 81/0.30 | 1.0 | 24/0.20 | 0.8 |  | 4.9 | 46.9 | 304 |
| 35 | 285/0.40 | 2.2 | 81/0.30 | 1.0 | 24/0.20 | 0.8 |  | 5.2 | 50.3 | 359 |
| 50 | 380/0.40 | 2.4 | 120/0.30 | 1.0 | 40/0.20 | 0.8 |  | 5.7 | 55.5 | 446 |
| 70 | 203/0.67 | 2.4 | 39/0.67 | 1.0 | 40/0.20 | 0.8 |  | 6.0 | 60.4 | 571 |
| 95 | 259/0.67 | 2.4 | 48/0.67 | 1.2 | 40/0.20 | 0.8 |  | 6.4 | 63.6 | 659 |
| 120 | 336/0.67 | 2.4 | 60/0.67 | 1.2 | 40/0.20 | 0.8 |  | 6.5 | 68.6 | 794 |
| 150 | 427/0.67 | 2.4 | 77/0.67 | 1.2 | 40/0.20 | 0.8 |  | 6.6 | 72.7 | 931 |
| 185 | 518/0.67 | 2.4 | 91/0.67 | 1.4 | 40/0.20 | 0.8 |  | 6.7 | 77.4 | 1080 |
| 240 | 672/0.67 | 2.4 | 119/0.67 | 1.4 | 40/0.20 | 0.8 |  | 6.9 | 83.4 | 1310 |
| 300 | 854/0.67 | 2.4 | 156/0.67 | 1.4 | 40/0.20 | 0.8 |  | 7.0 | 89.2 | 1570 |
| Type 441.6 Class1 |  |  |  |  |  |  |  |  |  |  |
| 16 | 126/0.40 | 3.0 | 81/0.30 | 1.0 | 24/0.20 | 0.8 |  | 5.0 | 47.4 | 276 |
| 25 | 209/0.40 | 3.0 | 81/0.30 | 1.0 | 24/0.20 | 0.8 |  | 5.3 | 51.2 | 350 |
| 35 | 285/0.40 | 3.0 | 81/0.30 | 1.0 | 24/0.20 | 0.8 |  | 5.6 | 54.6 | 405 |
| 50 | 380/0.40 | 3.0 | 120/0.30 | 1.2 | 40/0.20 | 0.8 |  | 6.0 | 58.7 | 485 |
| 70 | 203/0.67 | 3.0 | 39/0.67 | 1.2 | 40/0.20 | 0.8 |  | 6.3 | 63.7 | 634 |
| 95 | 259/0.67 | 3.0 | 48/0.67 | 1.2 | 40/0.20 | 0.8 |  | 6.4 | 66.5 | 700 |
| 120 | 336/0.67 | 3.0 | 60/0.67 | 1.2 | 40/0.20 | 0.8 |  | 6.6 | 71.4 | 835 |
| 150 | 427/0.67 | 3.0 | 77/0.67 | 1.2 | 40/0.20 | 0.8 |  | 6.7 | 75.5 | 975 |
| 185 | 518/0.67 | 3.0 | 91/0.67 | 1.4 | 40/0.20 | 0.8 |  | 6.8 | 80.3 | 1130 |
| 240 | 672/0.67 | 3.0 | 119/0.67 | 1.4 | 40/0.20 | 0.8 |  | 7.0 | 86.2 | 1360 |
| 300 | 854/0.67 | 3.0 | 156/0.67 | 1.4 | 40/0.20 | 0.8 |  | 7.1 | 92.0 | 1650 |
| Type 441.11 Class1 |  |  |  |  |  |  |  |  |  |  |
| 25 | 209/0.40 | 5.0 | 81/0.30 | 1.2 | 24/0.20 | 0.8 |  | 6.3 | 62.2 | 481 |

36	www.caledonian-cables.co.uk  www.addison-cables.com

Caledonian Mining Cables

AS/NZS 2802:2000 Reeling & Trailing Cables

| Nominal Conductor Area | Strand Size | Insulation Thickness | Earth Conductor |  | Pilot Conductor |  | Thickness of Sheath | Nominal Overall Diameter | Nominal Weight |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
|  |  |  | Strand Size | Thickness of Covering | Strand Size | Thickness of Covering |  |  |  |
| mm² | No/mm | mm | No/mm | mm | No/mm | mm | mm | mm | kg/100m |
| 35 | 285/0.40 | 5.0 | 81/0.30 | 1.4 | 24/0.20 | 0.8 | 6.4 | 65.2 | 542 |
| 50 | 380/0.40 | 5.0 | 120/0.30 | 1.4 | 40/0.20 | 0.8 | 6.5 | 68.6 | 620 |
| 70 | 203/0.67 | 5.0 | 39/0.67 | 1.4 | 40/0.20 | 0.8 | 6.6 | 73.1 | 750 |
| 95 | 259/0.67 | 5.0 | 48/0.67 | 1.4 | 40/0.20 | 0.8 | 6.8 | 76.2 | 850 |
| 120 | 336/0.67 | 5.0 | 60/0.67 | 1.4 | 40/0.20 | 0.8 | 6.9 | 80.9 | 986 |
| 150 | 427/0.67 | 5.0 | 77/0.67 | 1.4 | 40/0.20 | 0.8 | 7.0 | 85.0 | 1129 |
| 185 | 518/0.67 | 5.0 | 91/0.67 | 1.4 | 40/0.20 | 0.8 | 7.1 | 89.6 | 1289 |
| 240 | 672/0.67 | 5.0 | 119/0.67 | 1.4 | 40/0.20 | 0.8 | 7.3 | 95.7 | 1539 |
| Type 441.22 Class1 |  |  |  |  |  |  |  |  |  |
| 35 | 285/0.40 | 7.6 | 81/0.30 | 1.8 | 24/0.20 | 0.8 | 6.9 | 77.9 | 733 |
| 50 | 380/0.40 | 7.6 | 120/0.30 | 1.8 | 40/0.20 | 0.8 | 7.0 | 81.4 | 820 |
| 70 | 203/0.67 | 7.6 | 39/0.67 | 1.8 | 40/0.20 | 0.8 | 7.1 | 85.8 | 960 |
| 95 | 259/0.67 | 7.6 | 48/0.67 | 1.8 | 40/0.20 | 0.8 | 7.2 | 88.6 | 1070 |
| 120 | 336/0.67 | 7.6 | 60/0.67 | 1.8 | 40/0.20 | 0.8 | 7.3 | 93.4 | 1220 |
| 150 | 427/0.67 | 7.6 | 77/0.67 | 1.8 | 40/0.20 | 0.8 | 7.4 | 97.5 | 1380 |
| 185 | 518/0.67 | 7.6 | 91/0.67 | 1.8 | 40/0.20 | 0.8 | 7.6 | 102.4 | 1545 |

www.caledonian-cables.co.uk  www.addison-cables.com	37