Caledonian Mining Cables

AS/NZS 2802:2000 Reeling & Trailing Cables

Type 441 (class 2) 1.1/1.1KV

» Applications .............................................................................................................

These Class 2 cables are designed for many uses, suitable for trailing and also suitable for reeling applications, have one central pilot and a semiconductive cradle supporting and protecting the power cores, which makes these cables less likely to be damaged from crushing and squashing.

» Standards .................................................................................................................

AS/NZS 2802:2000

AS/NZS 1125

AS/NZS 3808

AS/NZS 5000.1

» Construction ............................................................................................................

Semiconductive PCP Filling And Covering Reinforcement

Stranded Tinned Copper Conductor EPR Insulation

Central Extensible Pilot Cradle Separator Insulation Screen  Earth Conductor

Heavy Duty PCP Sheath

3×Conductors: Flexible stranded tinned annealed copper conductor.

Insulation: EPR.

Insulation Screen: Semiconductive elastomer.

Cradle Separator: Semiconductive PCP.

Overall Core Screen: Semiconductive PCP filling and covering.

3×Interstitial Earth Conductor: Semiconductive PCP covered flexible stranded tinned copper conductor.

1×Central Extensible Pilot: EPR covered flexible stranded tinned copper conductor.

Textile Reinforcement: Open-weave braid reinforcement.

Sheath: Heavy duty PCP sheath. Heavy duty CPE/CSP sheath can be oﬀered upon request.

www.caledonian-cables.co.uk  www.addison-cables.com	33

Caledonian Mining Cables

AS/NZS 2802:2000 Reeling & Trailing Cables

»  Dimensions and Weight ..........................................................................................

| Nominal Conductor Area | Strand Size | Insulation Thickness | Earth Conductor |  | Pilot Conductor |  |  | Thickness of Sheath | Nominal Overall Diameter | Nominal Weight |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
|  |  |  | Strand Size | Thickness of Covering |  | Strand Size | Thickness of Covering |  |  |  |
| mm² | No/mm | mm | No/mm | mm |  | No/mm | mm | mm | mm | kg/100m |
| Type 441.1 Class2 |  |  |  |  |  |  |  |  |  |  |
| 6 | 84/0.30 | 1.5 | 33/0.30 | 0.8 |  | 24/0.20 | 0.8 | 3.8 | 28.5 | 111 |
| 10 | 77/0.40 | 1.5 | 51/0.30 | 0.8 |  | 24/0.20 | 0.8 | 3.8 | 31.1 | 136 |
| 16 | 126/0.40 | 1.6 | 81/0.30 | 1.0 |  | 24/0.20 | 0.8 | 3.9 | 34.1 | 176 |
| 25 | 209/0.40 | 1.6 | 81/0.30 | 1.0 |  | 24/0.20 | 0.8 | 4.2 | 37.9 | 231 |
| 35 | 285/0.40 | 1.6 | 81/0.30 | 1.0 |  | 24/0.20 | 0.8 | 4.4 | 41.2 | 274 |
| 50 | 380/0.40 | 1.7 | 120/0.30 | 1.0 |  | 40/0.20 | 0.8 | 4.9 | 45.9 | 349 |
| 70 | 203/0.67 | 1.8 | 39/0.67 | 1.0 |  | 40/0.20 | 0.8 | 5.3 | 52.2 | 481 |
| 95 | 259/0.67 | 2.0 | 48/0.67 | 1.0 |  | 40/0.20 | 0.8 | 5.8 | 56.7 | 579 |
| 120 | 336/0.67 | 2.1 | 60/0.67 | 1.0 |  | 40/0.20 | 0.8 | 6.3 | 62.7 | 724 |
| 150 | 427/0.67 | 2.3 | 77/0.67 | 1.2 |  | 40/0.20 | 0.8 | 6.7 | 68.3 | 881 |
| 185 | 518/0.67 | 2.5 | 91/0.67 | 1.2 |  | 40/0.20 | 0.8 | 7.3 | 74.9 | 1049 |
| 240 | 672/0.67 | 2.8 | 119/0.67 | 1.2 |  | 40/0.20 | 0.8 | 8.0 | 83.3 | 1329 |
| 300 | 854/0.67 | 3.0 | 156/0.67 | 1.4 |  | 40/0.20 | 0.8 | 8.7 | 91.2 | 1629 |

34	www.caledonian-cables.co.uk  www.addison-cables.com