Caledonian Mining Cables

AS/NZS 2802:2000 Reeling & Trailing Cables

Type 455 3.3 to 33KV

» Applications .............................................................................................................

These cables are designed with reduced insulation and sheath thickness, no cradle, 2 earth and 1 pilot core (each earth and pilot are the same size) in the outer interstices. These cables are suitable for reeling and trailing applications where minimal diameter and mass is desired, particularly suited to stacker-reclaimer applications.

» Standards .................................................................................................................

AS/NZS 2802:2000

AS/NZS 1125

AS/NZS 3808

AS/NZS 5000.1

» Construction ............................................................................................................

Interstitial Earth Conductor Reinforcement

Stranded Tinned Copper Conductor

Conductor Screen Centre Filler

EPR Insulation Insulation Screen Interstitial Pilot

Extra-heavy Duty PCP Sheath

3×Conductors: Flexible stranded tinned annealed copper conductor.

Conductor Screen: Semiconductive compound (for cables having a voltage rating of 3.3/3.3kV and above).

Insulation: EPR.

Insulation Screen: Semiconductive elastomer.

Filler: Elastomer centre filler.

2×Interstitial Earth Conductor: CSP covered flexible stranded tinned copper conductor.

1×Interstitial Pilot: EPR covered flexible stranded tinned copper conductor.

Textile Reinforcement: Open-weave braid reinforcement.

Sheath: Extra-heavy duty PCP sheath. Extra-heavy duty CPE/CSP sheath can be oﬀered upon request.

www.caledonian-cables.co.uk  www.addison-cables.com	41

Caledonian Mining Cables

AS/NZS 2802:2000 Reeling & Trailing Cables

»  Dimensions and Weight ..........................................................................................

| Nominal Conductor Area | Strand Size | Insulation Thickness | Pilot/Earth Conductor |  | Thickness of Sheath | Nominal Overall Diameter | Nominal Weight |
| --- | --- | --- | --- | --- | --- | --- | --- |
|  |  |  | Strand Size | Thickness of Covering |  |  |  |
| mm² | No/mm | mm | No/mm | mm | mm | mm | kg/100m |
| Type 455.3 Class1 |  |  |  |  |  |  |  |
| 16 | 126/0.40 | 2.2 | 120/0.30 | 1.4 | 4.2 | 39.4 | 224 |
| 25 | 209/0.40 | 2.2 | 120/0.30 | 1.4 | 4.5 | 43.3 | 281 |
| 35 | 285/0.40 | 2.2 | 120/0.30 | 1.4 | 4.8 | 46.7 | 336 |
| 50 | 380/0.40 | 2.4 | 183/0.30 | 1.4 | 5.3 | 51.9 | 424 |
| 70 | 203/0.67 | 2.4 | 54/0.67 | 1.4 | 5.7 | 57.0 | 556 |
| 95 | 259/0.67 | 2.4 | 70/0.67 | 1.6 | 6.1 | 60.5 | 646 |
| 120 | 336/0.67 | 2.4 | 84/0.67 | 1.6 | 6.4 | 65.6 | 786 |
| 150 | 427/0.67 | 2.4 | 112/0.67 | 1.6 | 6.5 | 69.7 | 931 |
| 185 | 518/0.67 | 2.4 | 132/0.67 | 1.6 | 6.6 | 74.5 | 1072 |
| 240 | 672/0.67 | 2.4 | 168/0.67 | 1.6 | 6.8 | 80.5 | 1310 |
| 300 | 854/0.67 | 2.4 | 228/0.67 | 1.6 | 6.9 | 86.3 | 1600 |
| Type 455.6 Class1 |  |  |  |  |  |  |  |
| 16 | 126/0.40 | 3.0 | 120/0.30 | 1.4 | 4.7 | 43.9 | 266 |
| 25 | 209/0.40 | 3.0 | 120/0.30 | 1.6 | 5.0 | 47.8 | 332 |
| 35 | 285/0.40 | 3.0 | 120/0.30 | 1.6 | 5.3 | 51.3 | 387 |
| 50 | 380/0.40 | 3.0 | 183/0.30 | 1.6 | 5.6 | 55.1 | 466 |
| 70 | 203/0.67 | 3.0 | 54/0.67 | 1.6 | 6.0 | 60.3 | 597 |
| 95 | 259/0.67 | 3.0 | 70/0.67 | 1.8 | 6.3 | 63.5 | 692 |
| 120 | 336/0.67 | 3.0 | 84/0.67 | 1.8 | 6.5 | 68.5 | 826 |
| 150 | 427/0.67 | 3.0 | 112/0.67 | 1.8 | 6.6 | 72.6 | 977 |
| 185 | 518/0.67 | 3.0 | 132/0.67 | 1.8 | 6.7 | 77.3 | 1122 |
| 240 | 672/0.67 | 3.0 | 168/0.67 | 1.8 | 6.9 | 83.3 | 1361 |
| 300 | 854/0.67 | 3.0 | 228/0.67 | 1.8 | 7.0 | 89.1 | 1652 |
| Type 455.11 Class1 |  |  |  |  |  |  |  |
| 16 | 126/0.40 | 5.0 | 120/0.30 | 2.0 | 5.8 | 55.1 | 392 |
| 25 | 209/0.40 | 5.0 | 120/0.30 | 2.0 | 6.1 | 59.0 | 462 |
| 35 | 285/0.40 | 5.0 | 120/0.30 | 2.0 | 6.3 | 62.2 | 527 |
| 50 | 380/0.40 | 5.0 | 183/0.30 | 2.0 | 6.4 | 65.6 | 607 |
| 70 | 203/0.67 | 5.0 | 54/0.67 | 2.0 | 6.5 | 70.2 | 742 |
| 95 | 259/0.67 | 5.0 | 70/0.67 | 2.2 | 6.7 | 73.2 | 837 |
| 120 | 336/0.67 | 5.0 | 84/0.67 | 2.2 | 6.8 | 77.9 | 982 |
| 150 | 427/0.67 | 5.0 | 112/0.67 | 2.2 | 6.9 | 82.0 | 1143 |
| 185 | 518/0.67 | 5.0 | 132/0.67 | 2.2 | 7.0 | 86.8 | 1305 |
| 240 | 672/0.67 | 5.0 | 168/0.67 | 2.2 | 7.2 | 92.8 | 1553 |
| Type 455.22 Class1 |  |  |  |  |  |  |  |
| 16 | 126/0.40 | 7.6 | 120/0.30 | 2.5 | 6.6 | 68.5 | 578 |
| 25 | 209/0.40 | 7.6 | 120/0.30 | 2.5 | 6.6 | 71.7 | 653 |
| 35 | 285/0.40 | 7.6 | 120/0.30 | 2.5 | 6.7 | 74.7 | 719 |

42	www.caledonian-cables.co.uk  www.addison-cables.com

Caledonian Mining Cables

AS/NZS 2802:2000 Reeling & Trailing Cables

| Nominal Conductor Area | Strand Size | Insulation Thickness | Pilot/Earth Conductor |  | Thickness of Sheath | Nominal Overall Diameter | Nominal Weight |
| --- | --- | --- | --- | --- | --- | --- | --- |
|  |  |  | Strand Size | Thickness of Covering |  |  |  |
| mm² | No/mm | mm | No/mm | mm | mm | mm | kg/100m |
| 50 | 380/0.40 | 7.6 | 183/0.30 | 2.5 | 6.8 | 78.2 | 810 |
| 70 | 203/0.67 | 7.6 | 54/0.67 | 2.5 | 7.0 | 82.9 | 956 |
| 95 | 259/0.67 | 7.6 | 70/0.67 | 2.5 | 7.1 | 85.7 | 1061 |
| 120 | 336/0.67 | 7.6 | 84/0.67 | 2.5 | 7.2 | 90.5 | 1221 |
| 150 | 427/0.67 | 7.6 | 112/0.67 | 2.5 | 7.3 | 94.6 | 1392 |
| 185 | 518/0.67 | 7.6 | 132/0.67 | 2.5 | 7.4 | 99.3 | 1564 |
| Type 455.33 Class1 |  |  |  |  |  |  |  |
| 16 | 126/0.40 | 10.5 | 120/0.30 | 2.5 | 7.0 | 83.0 | 822 |
| 25 | 209/0.40 | 10.5 | 120/0.30 | 2.5 | 7.1 | 86.4 | 920 |
| 35 | 285/0.40 | 10.5 | 120/0.30 | 2.5 | 7.2 | 89.4 | 993 |
| 50 | 380/0.40 | 10.5 | 183/0.30 | 2.5 | 7.3 | 92.8 | 1092 |
| 70 | 203/0.67 | 10.5 | 54/0.67 | 2.5 | 7.4 | 97.4 | 1254 |
| 95 | 259/0.67 | 10.5 | 70/0.67 | 2.5 | 7.6 | 100.4 | 1372 |
| 120 | 336/0.67 | 10.5 | 84/0.67 | 2.5 | 7.7 | 105.1 | 1543 |
| 150 | 427/0.67 | 10.5 | 112/0.67 | 2.5 | 7.8 | 109.2 | 1720 |

www.caledonian-cables.co.uk  www.addison-cables.com	43