Caledonian Mining Cables

AS/NZS 1972:2006 Cables

XLPE Insulated 6.35/11KV & 12.7/22KV

» Applications .............................................................................................................

These cables are used as HV feeder cables in fixed conditions.

» Standards .................................................................................................................

AS/NZS 1972:2006

AS/NZS 1125

AS/NZS 3808

» Construction ............................................................................................................

Conductors: Stranded plain copper conductor.

Insulation: XLPE.

Individual Screen (earth conductor): Copper wire.

Inner Sheath: PVC sheath.

Armour: Galvanized steel wire armour.

Outer Sheath: PVC sheath to AS/NZS 1429.1.

Stranded Copper Conductor XLPE Insulation

Filler

Copper Wire Screen Inner PVC Sheath

Galvanized Steel Wire Armour Outer PVC Sheath

»  Dimensions and Weight ..........................................................................................

| Nominal Conductor Area | Nominal Conductor Diameter | Insulation Thickness | Core Screen |  | Armour Wire Diameter | Nominal Sheath Thickness | Nominal Overall Diameter | Nominal Weight |
| --- | --- | --- | --- | --- | --- | --- | --- | --- |
|  |  |  | Strand Size | Area of Screen |  |  |  |  |
| mm² | mm | mm | mm | mm² | mm | mm | mm | kg/100m |
| 6.35/11kV |  |  |  |  |  |  |  |  |
| 16 | 4.8 | 3.4 | 10/0.85 | 5.7 | 2.00 | 2.4 | 46.6 | 330 |

www.caledonian-cables.co.uk  www.addison-cables.com	51

Caledonian Mining Cables

AS/NZS 1972:2006 Cables

| Nominal Conductor Area | Nominal Conductor Diameter | Insulation Thickness | Core Screen |  | Armour Wire Diameter | Nominal Sheath Thickness | Nominal Overall Diameter | Nominal Weight |
| --- | --- | --- | --- | --- | --- | --- | --- | --- |
|  |  |  | Strand Size | Area of Screen |  |  |  |  |
| mm² | mm | mm | mm | mm² | mm | mm | mm | kg/100m |
| 25 | 5.8 | 3.4 | 10/0.85 | 5.7 | 2.50 | 2.5 | 50.1 | 415 |
| 35 | 6.8 | 3.4 | 11/0.85 | 6.2 | 2.50 | 2.6 | 52.8 | 475 |
| 50 | 8.0 | 3.4 | 15/0.85 | 8.5 | 2.50 | 2.7 | 55.7 | 540 |
| 70 | 9.6 | 3.4 | 21/0.85 | 11.9 | 2.50 | 2.8 | 59.6 | 645 |
| 95 | 11.5 | 3.4 | 29/0.85 | 16.5 | 2.50 | 2.9 | 63.9 | 775 |
| 120 | 13.1 | 3.4 | 36/0.85 | 20.4 | 2.50 | 3.1 | 67.9 | 905 |
| 150 | 14.5 | 3.4 | 44/0.85 | 25.0 | 2.50 | 3.2 | 71.5 | 1030 |
| 185 | 16.1 | 3.4 | 22/1.35 | 31.5 | 3.15 | 3.3 | 78.6 | 1280 |
| 240 | 18.5 | 3.4 | 29/1.35 | 41.5 | 3.15 | 3.5 | 84.7 | 1550 |
| 300 | 20.7 | 3.4 | 37/1.35 | 53.0 | 3.15 | 3.7 | 90.4 | 1820 |
| 400 | 23.6 | 3.4 | 47/1.35 | 67.3 | 3.15 | 4.0 | 97.9 | 2230 |
| 12.7/22kV |  |  |  |  |  |  |  |  |
| 35 | 6.8 | 5.5 | 14/0.85 | 7.9 | 2.5 | 2.9 | 63.2 | 600 |
| 50 | 8.0 | 5.5 | 15/0.85 | 8.5 | 2.5 | 3.0 | 66.0 | 665 |
| 70 | 9.6 | 5.5 | 21/0.85 | 11.9 | 2.5 | 3.1 | 69.9 | 775 |
| 95 | 11.5 | 5.5 | 29/0.85 | 16.5 | 2.5 | 3.3 | 74.4 | 920 |
| 120 | 13.1 | 5.5 | 36/0.85 | 20.4 | 3.15 | 3.4 | 79.5 | 1140 |
| 150 | 14.5 | 5.5 | 44/0.85 | 25.0 | 3.15 | 3.5 | 83.1 | 1280 |
| 185 | 16.1 | 5.5 | 22/1.35 | 31.5 | 3.15 | 3.7 | 89.1 | 1450 |
| 240 | 18.5 | 5.5 | 29/1.35 | 41.5 | 3.15 | 3.9 | 95.0 | 1720 |
| 300 | 20.7 | 5.5 | 37/1.35 | 53.0 | 3.15 | 4.1 | 101.1 | 2010 |
| 400 | 23.6 | 5.5 | 47/1.35 | 67.3 | 3.15 | 4.3 | 108.2 | 2420 |

52	www.caledonian-cables.co.uk  www.addison-cables.com