Caledonian Mining Cables

AS/NZS 1802:2003 Reeling & Trailing Cables

Type 240 1.1 to 11KV

» Applications .............................................................................................................

These cables are mainly used as feeder cables for power supply to machinery or longwall supply. Cable contains 3 large pilots and large Core Screens provide for low resistance earthing.

» Standards .................................................................................................................

AS/NZS 1802:2003

AS/NZS 1125

AS/NZS 3808

AS/NZS 5000.1

» Construction ............................................................................................................

Composite Screen

Stranded Tinned Copper Conductor Conductor Screen

Interstitial Pilot Cradle Separator EPR Insulation Insulation Screen

Heavy Duty PCP Sheath

3×Conductors: Flexible stranded tinned annealed copper conductor.

Conductor Screen: Semiconductive compound (for cables having a voltage rating of 3.3/3.3kV and above).

Insulation: EPR.

Insulation Screen: Semiconductive elastomer.

Composite Screen (earth conductor): Tinned annealed copper braiding interwove with polyester yarn.

3×Interstitial Pilot: EPR covered flexible stranded tinned copper conductor.

Cradle Separator: Semiconductive PCP.

Sheath: Heavy duty PCP sheath. Heavy duty CPE/CSP sheath can be oﬀered upon request.

10	www.caledonian-cables.co.uk  www.addison-cables.com

Caledonian Mining Cables

AS/NZS 1802:2003 Reeling & Trailing Cables

»  Dimensions and Weight ..........................................................................................

| Nominal Conductor Area | Strand Size | Insulation Thickness | Core Screen |  | Pilot Conductor |  | Thickness of Sheath | Nominal Overall Diameter | Nominal Weight |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
|  |  |  | Strand Size | Area of Screen | Strand Size | Thickness of Covering |  |  |  |
| mm² | No/mm | mm | No/mm | mm² | No/mm | mm | mm | mm | kg/100m |
| Type 240.1 |  |  |  |  |  |  |  |  |  |
| 6 | 84/0.30 | 1.5 | 7/0.25 | 7.2 | 18/0.30 | 1.0 | 3.8 | 30.0 | 131 |
| 10 | 77/0.40 | 1.5 | 7/0.25 | 8.6 | 27/0.30 | 1.0 | 3.8 | 32.6 | 159 |
| 16 | 126/0.40 | 1.6 | 7/0.25 | 9.6 | 42/0.30 | 1.0 | 4.0 | 35.8 | 202 |
| 25 | 209/0.40 | 1.6 | 7/0.25 | 11.3 | 66/0.30 | 1.2 | 4.3 | 39.7 | 265 |
| 35 | 285/0.40 | 1.6 | 7/0.25 | 12.4 | 90/0.30 | 1.2 | 4.6 | 43.1 | 326 |
| 50 | 380/0.40 | 1.7 | 7/0.25 | 14.1 | 120/0.30 | 1.2 | 5.0 | 47.7 | 404 |
| 70 | 203/0.67 | 1.8 | 7/0.25 | 16.5 | 39/0.67 | 1.2 | 5.4 | 53.9 | 533 |
| 95 | 259/0.67 | 2.0 | 7/0.25 | 18.2 | 39/0.67 | 1.2 | 6.0 | 58.6 | 635 |
| 120 | 336/0.67 | 2.1 | 7/0.25 | 20.3 | 42/0.67 | 1.4 | 6.4 | 64.4 | 775 |
| 150 | 427/0.67 | 2.3 | 7/0.25 | 22.3 | 54/0.67 | 1.4 | 6.9 | 70.2 | 940 |
| 185 | 518/0.67 | 2.5 | 7/0.30 | 30.2 | 63/0.67 | 1.4 | 7.4 | 77.4 | 1150 |
| 240 | 672/0.67 | 2.8 | 7/0.30 | 33.6 | 77/0.67 | 1.6 | 8.2 | 86.0 | 1440 |
| 300 | 854/0.67 | 3.0 | 7/0.40 | 50.1 | 98/0.67 | 1.6 | 8.8 | 95.1 | 1810 |
| Type 240.3 |  |  |  |  |  |  |  |  |  |
| 16 | 126/0.40 | 3.0 | 7/0.25 | 13.1 | 42/0.30 | 1.4 | 5.3 | 46.2 | 306 |
| 25 | 209/0.40 | 3.0 | 7/0.25 | 14.8 | 66/0.30 | 1.4 | 5.6 | 50.1 | 379 |
| 35 | 285/0.40 | 3.0 | 7/0.25 | 15.8 | 90/0.30 | 1.4 | 5.9 | 53.5 | 444 |
| 50 | 380/0.40 | 3.0 | 7/0.25 | 17.2 | 120/0.30 | 1.4 | 6.3 | 57.6 | 525 |
| 70 | 203/0.67 | 3.0 | 7/0.25 | 18.6 | 39/0.67 | 1.4 | 6.6 | 62.5 | 656 |
| 95 | 259/0.67 | 3.0 | 7/0.25 | 20.3 | 39/0.67 | 1.4 | 7.1 | 66.2 | 750 |
| 120 | 336/0.67 | 3.0 | 7/0.30 | 27.2 | 42/0.67 | 1.6 | 7.4 | 72.0 | 910 |
| 150 | 427/0.67 | 3.0 | 7/0.40 | 39.6 | 54/0.67 | 1.6 | 7.8 | 78.0 | 1115 |
| 185 | 518/0.67 | 3.0 | 7/0.40 | 42.2 | 63/0.67 | 1.8 | 8.2 | 83.4 | 1280 |
| 240 | 672/0.67 | 3.0 | 7/0.40 | 46.6 | 77/0.67 | 1.8 | 8.8 | 90.3 | 1540 |
| 300 | 854/0.67 | 3.0 | 7/0.50 | 63.2 | 98/0.67 | 1.8 | 9.4 | 98.4 | 1920 |
| Type 240.6 |  |  |  |  |  |  |  |  |  |
| 16 | 126/0.40 | 5.0 | 7/0.25 | 17.2 | 42/0.30 | 1.4 | 6.4 | 57.3 | 440 |
| 25 | 209/0.40 | 5.0 | 7/0.25 | 18.6 | 66/0.30 | 1.4 | 6.7 | 61.2 | 521 |

www.caledonian-cables.co.uk  www.addison-cables.com	11

Caledonian Mining Cables

AS/NZS 1802:2003 Reeling & Trailing Cables

| Nominal Conductor Area | Strand Size | Insulation Thickness | Core Screen |  | Pilot Conductor |  |  | Thickness of Sheath | Nominal Overall Diameter | Nominal Weight |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
|  |  |  | Strand Size | Area of Screen |  | Strand Size | Thickness of Covering |  |  |  |
| mm² | No/mm | mm | No/mm | mm² |  | No/mm | mm | mm | mm | kg/100m |
| 35 | 285/0.40 | 5.0 | 7/0.25 | 18.6 |  | 90/0.30 | 1.6 | 7.0 | 64.6 | 593 |
| 50 | 380/0.40 | 5.0 | 7/0.25 | 21.3 |  | 120/0.30 | 1.6 | 7.3 | 68.5 | 685 |
| 70 | 203/0.67 | 5.0 | 7/0.25 | 23.4 |  | 39/0.67 | 1.6 | 7.7 | 73.7 | 830 |
| 95 | 259/0.67 | 5.0 | 7/0.30 | 29.2 |  | 39/0.67 | 1.6 | 8.1 | 77.8 | 954 |
| 120 | 336/0.67 | 5.0 | 7/0.30 | 31.7 |  | 42/0.67 | 1.8 | 8.5 | 83.1 | 1111 |
| 150 | 427/0.67 | 5.0 | 7/0.40 | 45.7 |  | 54/0.67 | 1.8 | 8.9 | 89.1 | 1335 |
| 185 | 518/0.67 | 5.0 | 7/0.40 | 48.4 |  | 63/0.67 | 1.8 | 9.3 | 94.5 | 1515 |
| 240 | 672/0.67 | 5.0 | 7/0.40 | 52.8 |  | 77/0.67 | 1.8 | 9.9 | 101.4 | 1810 |
| 300 | 854/0.67 | 5.0 | 7/0.50 | 71.5 |  | 98/0.67 | 1.8 | 10.4 | 109.3 | 2190 |
| Type 240.11 |  |  |  |  |  |  |  |  |  |  |
| 25 | 209/0.40 | 7.6 | 7/0.25 | 23.7 |  | 66/0.30 | 2.0 | 8.1 | 75.6 | 752 |
| 35 | 285/0.40 | 7.6 | 7/0.30 | 30.2 |  | 90/0.30 | 2.0 | 8.4 | 79.7 | 860 |
| 50 | 380/0.40 | 7.6 | 7/0.30 | 31.7 |  | 120/0.30 | 2.0 | 8.7 | 83.6 | 961 |
| 70 | 203/0.67 | 7.6 | 7/0.30 | 34.1 |  | 39/0.67 | 2.0 | 9.1 | 88.8 | 1125 |
| 95 | 259/0.67 | 7.6 | 7/0.40 | 47.5 |  | 39/0.67 | 2.0 | 9.6 | 93.7 | 1300 |
| 120 | 336/0.67 | 7.6 | 7/0.40 | 51.0 |  | 42/0.67 | 2.2 | 9.9 | 98.8 | 1470 |
| 150 | 427/0.67 | 7.6 | 7/0.40 | 53.7 |  | 54/0.67 | 2.2 | 10.3 | 103.5 | 1659 |
| 185 | 518/0.67 | 7.6 | 7/0.40 | 57.2 |  | 63/0.67 | 2.2 | 10.7 | 108.8 | 1880 |

12	www.caledonian-cables.co.uk  www.addison-cables.com