Caledonian Mining Cables

AS/NZS 1802:2003 Reeling & Trailing Cables

Type 241 1.1 to 11KV

» Applications .............................................................................................................

These cables are designed for various uses, including main feeder cable for continuous miners, pump cable, and power supply cable. Overall semiconductive screen provides protective earth contact for any object breaching the sheath prior to contact with power conductors.

» Standards .................................................................................................................

AS/NZS 1802:2003

AS/NZS 1125

AS/NZS 3808

AS/NZS 5000.1

» Construction ............................................................................................................

Semiconductive PCP Filling And Covering Reinforcement

Stranded Tinned Copper Conductor

Conductor Screen Cradle Separator Central Extensible Pilot EPR Insulation Insulation Screen  Earth Conductor

Heavy Duty PCP Sheath

3×Conductors: Flexible stranded tinned annealed copper conductor.

Conductor Screen: Semiconductive compound (for cables having a voltage rating of 3.3/3.3kV and above).

Insulation: EPR.

Insulation Screen: Semiconductive elastomer.

Cradle Separator: Semiconductive PCP.

Overall Core Screen: Semiconductive PCP filling and covering.

3×Interstitial Earth Conductor: Semiconductive PCP covered flexible stranded tinned copper conductor.

1×Central Extensible Pilot: EPR covered flexible stranded tinned copper conductor.

Textile Reinforcement: Open-weave braid reinforcement.

www.caledonian-cables.co.uk  www.addison-cables.com	13

Caledonian Mining Cables

AS/NZS 1802:2003 Reeling & Trailing Cables

Sheath: Heavy duty PCP sheath. Heavy duty CPE/CSP sheath can be oﬀered upon request.

»  Dimensions and Weight ..........................................................................................

| Nominal Conductor Area | Strand Size | Insulation Thickness | Earth Conductor |  | Pilot Conductor |  | Thickness of Sheath Including SC PCP Layer |  | Nominal Overall Diameter | Nominal Weight |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
|  |  |  | Strand Size | Thickness of Covering | Strand Size | Thickness of Covering |  |  |  |  |
| mm² | No/mm | mm | No/mm | mm | No/mm | mm |  | mm | mm | kg/100m |
| Type 241.1 |  |  |  |  |  |  |  |  |  |  |
| 6 | 84/0.30 | 1.5 | 18/0.30 | 1.0 | 24/0.20 | 0.8 |  | 3.8 | 28.5 | 106 |
| 10 | 77/0.40 | 1.5 | 27/0.30 | 1.0 | 24/0.20 | 0.8 |  | 3.8 | 31.1 | 127 |
| 16 | 126/0.40 | 1.6 | 42/0.30 | 1.0 | 24/0.20 | 0.8 |  | 3.9 | 34.1 | 164 |
| 25 | 209/0.40 | 1.6 | 66/0.30 | 1.0 | 24/0.20 | 0.8 |  | 4.2 | 37.9 | 208 |
| 35 | 285/0.40 | 1.6 | 90/0.30 | 1.0 | 24/0.20 | 0.8 |  | 4.4 | 41.2 | 254 |
| 50 | 380/0.40 | 1.7 | 120/0.30 | 1.0 | 40/0.20 | 0.8 |  | 4.9 | 45.9 | 328 |
| 70 | 203/0.67 | 1.8 | 39/0.67 | 1.0 | 40/0.20 | 0.8 |  | 5.3 | 52.2 | 480 |
| 95 | 259/0.67 | 2.0 | 39/0.67 | 1.0 | 40/0.20 | 0.8 |  | 5.8 | 56.7 | 600 |
| 120 | 336/0.67 | 2.1 | 42/0.67 | 1.2 | 40/0.20 | 0.8 |  | 6.3 | 62.7 | 710 |
| 150 | 427/0.67 | 2.3 | 54/0.67 | 1.2 | 40/0.20 | 0.8 |  | 6.7 | 68.3 | 865 |
| 185 | 518/0.67 | 2.5 | 63/0.67 | 1.4 | 40/0.20 | 0.8 |  | 7.3 | 74.9 | 1030 |
| 240 | 672/0.67 | 2.8 | 77/0.67 | 1.4 | 40/0.20 | 0.8 |  | 8.0 | 83.3 | 1300 |
| 300 | 854/0.67 | 3.0 | 98/0.67 | 1.4 | 40/0.20 | 0.8 |  | 8.7 | 91.2 | 1600 |
| Type 241.3 |  |  |  |  |  |  |  |  |  |  |
| 16 | 126/0.40 | 3.0 | 42/0.30 | 1.0 | 24/0.20 | 0.8 |  | 5.0 | 43.8 | 249 |
| 25 | 209/0.40 | 3.0 | 66/0.30 | 1.0 | 24/0.20 | 0.8 |  | 5.3 | 47.7 | 315 |
| 35 | 285/0.40 | 3.0 | 90/0.30 | 1.0 | 24/0.20 | 0.8 |  | 5.6 | 51.1 | 376 |
| 50 | 380/0.40 | 3.0 | 120/0.30 | 1.2 | 40/0.20 | 0.8 |  | 6.0 | 55.2 | 450 |
| 70 | 203/0.67 | 3.0 | 39/0.67 | 1.2 | 40/0.20 | 0.8 |  | 6.4 | 60.3 | 576 |
| 95 | 259/0.67 | 3.0 | 48/0.67 | 1.2 | 40/0.20 | 0.8 |  | 6.8 | 63.8 | 675 |
| 120 | 336/0.67 | 3.0 | 60/0.67 | 1.2 | 40/0.20 | 0.8 |  | 7.2 | 69.1 | 810 |
| 150 | 427/0.67 | 3.0 | 77/0.67 | 1.2 | 40/0.20 | 0.8 |  | 7.6 | 73.8 | 952 |
| 185 | 518/0.67 | 3.0 | 91/0.67 | 1.4 | 40/0.20 | 0.8 |  | 8.0 | 79.2 | 1130 |
| 240 | 672/0.67 | 3.0 | 112/0.67 | 1.4 | 40/0.20 | 0.8 |  | 8.6 | 86.0 | 1380 |
| 300 | 854/0.67 | 3.0 | 144/0.67 | 1.4 | 40/0.20 | 0.8 |  | 9.1 | 92.6 | 1660 |

14	www.caledonian-cables.co.uk  www.addison-cables.com

Caledonian Mining Cables

AS/NZS 1802:2003 Reeling & Trailing Cables

| Nominal Conductor Area | Strand Size | Insulation Thickness | Earth Conductor |  | Pilot Conductor |  | Thickness of Sheath Including SC PCP Layer | Nominal Overall Diameter | Nominal Weight |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
|  |  |  | Strand Size | Thickness of Covering | Strand Size | Thickness of Covering |  |  |  |
| mm² | No/mm | mm | No/mm | mm | No/mm | mm | mm | mm | kg/100m |
| Type 241.6 |  |  |  |  |  |  |  |  |  |
| 16 | 126/0.40 | 5.0 | 42/0.30 | 1.4 | 24/0.20 | 0.8 | 6.1 | 54.9 | 365 |
| 25 | 209/0.40 | 5.0 | 66/0.30 | 1.4 | 24/0.20 | 0.8 | 6.4 | 58.8 | 440 |
| 35 | 285/0.40 | 5.0 | 90/0.30 | 1.4 | 24/0.20 | 0.8 | 6.7 | 62.2 | 509 |
| 50 | 380/0.40 | 5.0 | 120/0.30 | 1.4 | 40/0.20 | 0.8 | 7.1 | 66.2 | 592 |
| 70 | 203/0.67 | 5.0 | 39/0.67 | 1.4 | 40/0.20 | 0.8 | 7.4 | 71.2 | 727 |
| 95 | 259/0.67 | 5.0 | 48/0.67 | 1.4 | 40/0.20 | 0.8 | 7.9 | 74.8 | 835 |
| 120 | 336/0.67 | 5.0 | 60/0.67 | 1.4 | 40/0.20 | 0.8 | 8.3 | 80.2 | 990 |
| 150 | 427/0.67 | 5.0 | 77/0.67 | 1.4 | 40/0.20 | 0.8 | 8.6 | 84.6 | 1140 |
| 185 | 518/0.67 | 5.0 | 91/0.67 | 1.4 | 40/0.20 | 0.8 | 9.0 | 90.0 | 1311 |
| 240 | 672/0.67 | 5.0 | 119/0.67 | 1.4 | 40/0.20 | 0.8 | 9.6 | 96.8 | 1576 |
| 300 | 854/0.67 | 5.0 | 156/0.67 | 1.4 | 40/0.20 | 0.8 | 10.2 | 103.6 | 1900 |
| Type 241.11 |  |  |  |  |  |  |  |  |  |
| 25 | 209/0.40 | 7.6 | 66/0.30 | 1.8 | 24/0.20 | 0.8 | 7.8 | 73.2 | 645 |
| 35 | 285/0.40 | 7.6 | 90/0.30 | 1.8 | 24/0.20 | 0.8 | 8.1 | 76.6 | 724 |
| 50 | 380/0.40 | 7.6 | 120/0.30 | 1.8 | 40/0.20 | 0.8 | 8.5 | 80.6 | 825 |
| 70 | 203/0.67 | 7.6 | 39/0.67 | 1.8 | 40/0.20 | 0.8 | 8.9 | 85.7 | 975 |
| 95 | 259/0.67 | 7.6 | 48/0.67 | 1.8 | 40/0.20 | 0.8 | 9.3 | 89.1 | 1088 |
| 120 | 336/0.67 | 7.6 | 60/0.67 | 1.8 | 40/0.20 | 0.8 | 9.7 | 94.4 | 1258 |
| 150 | 427/0.67 | 7.6 | 77/0.67 | 1.8 | 40/0.20 | 0.8 | 10.0 | 98.9 | 1423 |
| 185 | 518/0.67 | 7.6 | 91/0.67 | 1.8 | 40/0.20 | 0.8 | 10.4 | 104.2 | 1610 |

www.caledonian-cables.co.uk  www.addison-cables.com	15