Caledonian Mining Cables

AS/NZS 1802:2003 Reeling & Trailing Cables

Type 260 1.1 to 11KV

» Applications .............................................................................................................

These armoured cables are mainly used as feeder cables for power supply where mechanical protection and strength is required, and also can be the feeder to machinery and i.e. transportable mining substation (sand mining).

» Standards .................................................................................................................

AS/NZS 1802:2003

AS/NZS 1125

AS/NZS 3808

AS/NZS 5000.1

» Construction ............................................................................................................

Interstitial Pilot

Stranded Tinned Copper Conductor Conductor Screen

EPR Insulation Cradle Separator Insulation Screen Composite Screen Inner PCP Sheath

Pliable Galvanized Steel Armour Outer Heavy Duty PCP Sheath

3×Conductors: Flexible stranded tinned annealed copper conductor.

Conductor Screen: Semiconductive compound (for cables having a voltage rating of 3.3/3.3kV and above).

Insulation: EPR.

Insulation Screen: Semiconductive elastomer.

Composite Screen (earth conductor): Tinned annealed copper braiding interwove with polyester yarn.

Cradle Separator: Semiconductive PCP.

3×Interstitial Pilot: EPR covered flexible stranded tinned copper conductor.

Inner Sheath: PCP sheath. CPE/CSP sheath can be oﬀered upon request.

20	www.caledonian-cables.co.uk  www.addison-cables.com

Caledonian Mining Cables

AS/NZS 1802:2003 Reeling & Trailing Cables

Pliable Armour: Galvanized low carbon (mild) steel strands.

Outer Sheath: Heavy duty PCP sheath. Heavy duty CPE/CSP sheath can be oﬀered upon request.

»  Dimensions and Weight ..........................................................................................

| Nominal Conductor Area | Strand Size | Insulation Thickness | Core Screen |  | Pilot Conductor |  | Pliable Armour Size | Thickness of Sheath |  | Nominal Overall Diameter | Nominal Weight |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
|  |  |  | Strand Size | Area of Screen | Strand Size | Thickness of Covering |  | Inner | Outer |  |  |
| mm² | No/mm | mm | No/mm | mm² | No/mm | mm | No/mm | mm | mm | mm | kg/100m |
| Type 260.1 |  |  |  |  |  |  |  |  |  |  |  |
| 6 | 84/0.30 | 1.5 | 7/0.25 | 7.2 | 18/0.30 | 1.0 | 7/0.45 | 2.0 | 3.8 | 36.9 | 230 |
| 10 | 77/0.40 | 1.5 | 7/0.25 | 8.6 | 27/0.30 | 1.0 | 7/0.45 | 2.0 | 3.8 | 39.5 | 265 |
| 16 | 126/0.40 | 1.6 | 7/0.25 | 9.6 | 42/0.30 | 1.0 | 7/0.90 | 2.5 | 4.0 | 46.5 | 410 |
| 25 | 209/0.40 | 1.6 | 7/0.25 | 11.3 | 66/0.30 | 1.2 | 7/0.90 | 2.5 | 4.3 | 50.4 | 495 |
| 35 | 285/0.40 | 1.6 | 7/0.25 | 12.4 | 90/0.30 | 1.2 | 7/0.90 | 2.5 | 4.6 | 53.8 | 576 |
| 50 | 380/0.40 | 1.7 | 7/0.25 | 14.1 | 120/0.30 | 1.2 | 7/0.90 | 2.5 | 5.0 | 58.4 | 679 |
| 70 | 203/0.67 | 1.8 | 7/0.25 | 16.5 | 39/0.67 | 1.2 | 7/0.90 | 2.5 | 5.4 | 64.6 | 837 |
| 95 | 259/0.67 | 2.0 | 7/0.25 | 18.2 | 39/0.67 | 1.2 | 7/0.90 | 3.5 | 6.0 | 71.4 | 1003 |
| 120 | 336/0.67 | 2.1 | 7/0.25 | 20.3 | 42/0.67 | 1.4 | 7/0.90 | 3.5 | 6.4 | 77.2 | 1176 |
| 150 | 427/0.67 | 2.3 | 7/0.25 | 22.3 | 54/0.67 | 1.4 | 7/0.90 | 3.5 | 6.9 | 83.0 | 1372 |
| 185 | 518/0.67 | 2.5 | 7/0.30 | 30.2 | 63/0.67 | 1.4 | 7/0.90 | 3.5 | 7.4 | 90.0 | 1610 |
| 240 | 672/0.67 | 2.8 | 7/0.30 | 33.6 | 77/0.67 | 1.6 | 7/1.25 | 4.5 | 8.2 | 103.0 | 2150 |
| 300 | 854/0.67 | 3.0 | 7/0.40 | 50.1 | 98/0.67 | 1.6 | 7/1.25 | 4.5 | 8.8 | 112.1 | 2590 |
| Type 260.3 |  |  |  |  |  |  |  |  |  |  |  |
| 16 | 126/0.40 | 3.0 | 7/0.25 | 13.1 | 42/0.30 | 1.4 | 7/0.90 | 2.5 | 5.3 | 56.9 | 566 |
| 25 | 209/0.40 | 3.0 | 7/0.25 | 14.8 | 66/0.30 | 1.4 | 7/0.90 | 2.5 | 5.6 | 60.8 | 661 |
| 35 | 285/0.40 | 3.0 | 7/0.25 | 15.8 | 90/0.30 | 1.4 | 7/0.90 | 3.5 | 5.9 | 66.3 | 779 |
| 50 | 380/0.40 | 3.0 | 7/0.25 | 17.2 | 120/0.30 | 1.4 | 7/0.90 | 3.5 | 6.3 | 70.4 | 886 |
| 70 | 203/0.67 | 3.0 | 7/0.25 | 18.6 | 39/0.67 | 1.4 | 7/0.90 | 3.5 | 6.6 | 75.3 | 1044 |
| 95 | 259/0.67 | 3.0 | 7/0.25 | 20.3 | 39/0.67 | 1.4 | 7/0.90 | 3.5 | 7.1 | 78.9 | 1156 |
| 120 | 336/0.67 | 3.0 | 7/0.30 | 27.2 | 42/0.67 | 1.6 | 7/0.90 | 3.5 | 7.4 | 84.7 | 1350 |
| 150 | 427/0.67 | 3.0 | 7/0.40 | 39.6 | 54/0.67 | 1.6 | 7/1.25 | 4.5 | 7.8 | 95.0 | 1779 |
| 185 | 518/0.67 | 3.0 | 7/0.40 | 42.2 | 63/0.67 | 1.8 | 7/1.25 | 4.5 | 8.2 | 100.4 | 1990 |
| 240 | 672/0.67 | 3.0 | 7/0.40 | 46.6 | 77/0.67 | 1.8 | 7/1.25 | 4.5 | 8.8 | 107.3 | 2300 |

www.caledonian-cables.co.uk  www.addison-cables.com	21

Caledonian Mining Cables

AS/NZS 1802:2003 Reeling & Trailing Cables

| Nominal Conductor Area | Strand Size | Insulation Thickness | Core Screen |  | Pilot Conductor |  | Pliable Armour Size | Thickness of Sheath |  | Nominal Overall Diameter | Nominal Weight |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
|  |  |  | Strand Size | Area of Screen | Strand Size | Thickness of Covering |  | Inner | Outer |  |  |
| mm² | No/mm | mm | No/mm | mm² | No/mm | mm | No/mm | mm | mm | mm | kg/100m |
| 300 | 854/0.67 | 3.0 | 7/0.50 | 63.2 | 98/0.67 | 1.8 | 7/1.25 | 4.5 | 9.4 | 115.4 | 2710 |
| Type 260.6 |  |  |  |  |  |  |  |  |  |  |  |
| 16 | 126/0.40 | 5.0 | 7/0.25 | 17.2 | 42/0.30 | 1.4 | 7/0.90 | 3.5 | 6.4 | 70.1 | 796 |
| 25 | 209/0.40 | 5.0 | 7/0.25 | 18.6 | 66/0.30 | 1.4 | 7/0.90 | 3.5 | 6.7 | 74.0 | 897 |
| 35 | 285/0.40 | 5.0 | 7/0.25 | 18.6 | 90/0.30 | 1.6 | 7/0.90 | 3.5 | 7.0 | 77.4 | 990 |
| 50 | 380/0.40 | 5.0 | 7/0.25 | 21.3 | 120/0.30 | 1.6 | 7/0.90 | 3.5 | 7.3 | 81.2 | 1102 |
| 70 | 203/0.67 | 5.0 | 7/0.25 | 23.4 | 39/0.67 | 1.6 | 7/1.25 | 4.5 | 7.7 | 90.7 | 1456 |
| 95 | 259/0.67 | 5.0 | 7/0.30 | 29.2 | 39/0.67 | 1.6 | 7/1.25 | 4.5 | 8.1 | 94.8 | 1610 |
| 120 | 336/0.67 | 5.0 | 7/0.30 | 31.7 | 42/0.67 | 1.8 | 7/1.25 | 4.5 | 8.5 | 100.2 | 1807 |
| 150 | 427/0.67 | 5.0 | 7/0.40 | 45.7 | 54/0.67 | 1.8 | 7/1.25 | 4.5 | 8.9 | 106.2 | 2080 |
| 185 | 518/0.67 | 5.0 | 7/0.40 | 48.4 | 63/0.67 | 1.8 | 7/1.25 | 4.5 | 9.3 | 111.5 | 2300 |
| 240 | 672/0.67 | 5.0 | 7/0.40 | 52.8 | 77/0.67 | 1.8 | 7/1.25 | 4.5 | 9.9 | 118.4 | 2630 |
| 300 | 854/0.67 | 5.0 | 7/0.50 | 71.5 | 98/0.67 | 1.8 | 7/1.25 | 4.5 | 10.4 | 126.3 | 3060 |
| Type 260.11 |  |  |  |  |  |  |  |  |  |  |  |
| 25 | 209/0.40 | 7.6 | 7/0.25 | 23.7 | 66/0.30 | 2.0 | 7/1.25 | 4.5 | 8.1 | 92.7 | 1380 |
| 35 | 285/0.40 | 7.6 | 7/0.30 | 30.2 | 90/0.30 | 2.0 | 7/1.25 | 4.5 | 8.4 | 96.7 | 1528 |
| 50 | 380/0.40 | 7.6 | 7/0.30 | 31.7 | 120/0.30 | 2.0 | 7/1.25 | 4.5 | 8.7 | 100.6 | 1664 |
| 70 | 203/0.67 | 7.6 | 7/0.30 | 34.1 | 39/0.67 | 2.0 | 7/1.25 | 4.5 | 9.1 | 105.8 | 1867 |
| 95 | 259/0.67 | 7.6 | 7/0.40 | 47.5 | 39/0.67 | 2.0 | 7/1.25 | 4.5 | 9.6 | 110.7 | 2080 |
| 120 | 336/0.67 | 7.6 | 7/0.40 | 51.0 | 42/0.67 | 2.2 | 7/1.25 | 4.5 | 9.9 | 115.8 | 2290 |
| 150 | 427/0.67 | 7.6 | 7/0.40 | 53.7 | 54/0.67 | 2.2 | 7/1.25 | 4.5 | 10.3 | 120.5 | 2510 |
| 185 | 518/0.67 | 7.6 | 7/0.40 | 57.2 | 63/0.67 | 2.2 | 7/1.25 | 4.5 | 10.7 | 125.9 | 2750 |

22	www.caledonian-cables.co.uk  www.addison-cables.com