Caledonian Mining Cables

Portable Power Cables

Type G-GC Three-Conductor Round Portable Power Cable 2kV

� Applications .............................................................................................................

These cables are suitable for use with mobile mining equipment such as continuous miners, drills, cutters, loading machines, AC shuttle cars and pumps� Type G-GC is for applications where grounding conductors and a ground check conductor are required�

�  Standards

................................................................................................................

ICEA S-75-381/NEMA WC 58 ASTM B 172

ASTM B 33

CAN/CSA-C22�2 No�96

� Construction ............................................................................................................

Ground Check Conductor

Stranded Tinned Copper Conductor EPR Insulation

Grounding Conductor Reinforced CPE Jacket

Conductors:

Stranded annealed tinned copper conductor�

Insulation:

Ethylene Propylene Rubber (EPR)�

Ground Check Conductor:

Tinned copper conductor with a yellow polypropylene insulation�

Grounding Conductor:

Tinned copper conductor with an optional green outer covering�

www.caledonian-cables.co.uk  www.addison-cables.com	25

Caledonian Mining Cables

Portable Power Cables

Jacket:

Reinforced heavy-duty/extra-heavy-duty Chlorinated Polyethylene (CPE), black� (Cables having a nominal outside diameter of more than 2�0 inches require extra-heavy-duty jackets�)

� Options .....................................................................................................................

Other jacket materials such as CSP/PCP/NBR/PVC are available upon request�

Two-layer jacket with reinforcing fibre between the two layers can be oﬀered  as an option�

�  Mechanical and Thermal Properties ......................................................................

Minimum Bending Radius: 6�OD

Maximum Conductor Operating Temperature: +90℃

�  Dimensions and Weight

........................................................................................

| Construction | No. of Strands | Grounding Conductor Size | Ground Check Conductor Size | Nominal Insulation Thickness | Nominal Jacket Thickness | Nominal Overall Diameter | Nominal Weight | Ampacity |
| --- | --- | --- | --- | --- | --- | --- | --- | --- |
| No. of cores�AWG/ kcmil | - | AWG/ kcmil | AWG/ kcmil | inch | mm | inch | mm | inch | mm | lbs/kft | kg/km | A |
| 3�8 | 133 | 10 | 10 | 0�06 | 1�5 | 0�125 | 3�2 | 0�97 | 24�6 | 600 | 893 | 59 |
| 3�6 | 133 | 10 | 10 | 0�06 | 1�5 | 0�140 | 3�6 | 1�05 | 26�7 | 735 | 1094 | 79 |
| 3�4 | 259 | 8 | 10 | 0�06 | 1�5 | 0�155 | 3�9 | 1�19 | 30�2 | 1065 | 1585 | 104 |
| 3�3 | 259 | 8 | 10 | 0�06 | 1�5 | 0�155 | 3�9 | 1�25 | 31�8 | 1245 | 1853 | 120 |
| 3�2 | 259 | 7 | 10 | 0�06 | 1�5 | 0�155 | 3�9 | 1�34 | 34�0 | 1480 | 2202 | 138 |
| 3�1 | 259 | 6 | 8 | 0�08 | 2�0 | 0�170 | 4�3 | 1�51 | 38�4 | 1885 | 2805 | 161 |
| 3�1/0 | 266 | 5 | 8 | 0�08 | 2�0 | 0�170 | 4�3 | 1�65 | 41�9 | 2290 | 3408 | 186 |
| 3�2/0 | 329 | 4 | 8 | 0�08 | 2�0 | 0�190 | 4�8 | 1�75 | 44�5 | 2710 | 4033 | 215 |
| 3�3/0 | 418 | 2 | 8 | 0�08 | 2�0 | 0�190 | 4�8 | 1�89 | 48�0 | 3270 | 4866 | 249 |
| 3�4/0 | 532 | 2 | 8 | 0�08 | 2�0 | 0�205 | 5�2 | 2�04 | 51�8 | 3975 | 5915 | 287 |
| 3�250 | 627 | 2 | 6 | 0�095 | 2�4 | 0�220 | 5�6 | 2�39 | 60�7 | 4950 | 7366 | 320 |
| 3�350 | 888 | 1/0 | 6 | 0�095 | 2�4 | 0�235 | 6�0 | 2�68 | 68�1 | 6625 | 9859 | 394 |
| 3�500 | 1221 | 2/0 | 6 | 0�095 | 2�4 | 0�250 | 6�4 | 3�03 | 77�0 | 8890 | 13230 | 487 |

Ampacity-Based on a conductor temperature of 90℃ and an ambient air temperature of 40℃, per ICEA S-75-381�

26	www.caledonian-cables.co.uk  www.addison-cables.com