Caledonian Mining Cables

Portable Power Cables

Type SHD Three-Conductor Flat Portable Power Cable 2kV

» Applications .............................................................................................................

These flat parallel cables are designed for use on continuous miners requiring grounding conductors and metallic shielding over each conductor�

»  Standards

................................................................................................................

ICEA S-75-381/NEMA WC 58 ASTM B 172

ASTM B 33

CAN/CSA C22�2 No� 96

» Construction ............................................................................................................

Stranded Tinned Copper Conductor

Grounding Conductor

EPR Insulation

Insulation Shield

Reinforced CPE Jacket

Conductors:

Stranded annealed tinned copper conductor�

Insulation:

Ethylene Propylene Rubber (EPR)�

Insulation  Shield:  Tinned copper/textile braid� Grounding  Conductor:

Tinned copper conductor covered with a conducting extrusion layer�

Grounding Conductor

www.caledonian-cables.co.uk  www.addison-cables.com	27

Caledonian Mining Cables

Portable Power Cables

Jacket:

Reinforced extra-heavy-duty Chlorinated Polyethylene (CPE), black�

» Options .....................................................................................................................

- Other jacket materials such as CSP/PCP/NBR/PVC are available upon request�

- Two-layer jacket with reinforcing fibre between the two layers can be oﬀered  as an option�

»  Mechanical and Thermal Properties ......................................................................

Minimum Bending Radius: 6×OD

Maximum Conductor Operating Temperature: +90℃

»  Dimensions and Weight

........................................................................................

| Construction | No. of Strands | Grounding Conductor Size | Nominal Insulation Thickness |  | Nominal Jacket Thickness |  | Nominal Overall Diameter Height×Width |  | Nominal Weight |  | Ampacity |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
| No. of cores×AWG/ kcmil | - | AWG/kcmil | inch | mm | inch | mm | inch | mm | lbs/kft | kg/km | A |
| 3×2 | 259 | 6 | 0�07 | 1�8 | 0�125 | 3�2 | 0�94×2�45 | 23�9×62�2 | 2243 | 3338 | 159 |
| 3×1 | 259 | 5 | 0�08 | 2�0 | 0�140 | 3�6 | 1�04×2�64 | 26�4×67�1 | 2540 | 3780 | 184 |
| 3×1/0 | 259 | 4 | 0�08 | 2�0 | 0�140 | 3�6 | 1�08×2�82 | 27�4×71�6 | 2915 | 4338 | 211 |
| 3×2/0 | 329 | 3 | 0�08 | 2�0 | 0�155 | 3�9 | 1�18×2�99 | 30�0×76�0 | 3346 | 4980 | 243 |
| 3×3/0 | 413 | 2 | 0�08 | 2�0 | 0�155 | 3�9 | 1�25×3�29 | 31�8×83�6 | 3890 | 5789 | 279 |

Ampacity-Based on a conductor temperature of 90℃ and an ambient air temperature of 40℃, per ICEA S-75-381�

28	www.caledonian-cables.co.uk  www.addison-cables.com