Caledonian Mining Cables

Portable Power Cables

Grounding  Conductor: Tinned copper conductor� Jacket:

Thermoplastic Polyurethane (TPU) Jacket, black�

» Options .....................................................................................................................

- Other jacket materials such as CPE/CSP/PCP/NBR/PVC are available upon request�

- Two-layer jacket with reinforcing fibre between the two layers can be oﬀered  as an option�

»  Mechanical and Thermal Properties ......................................................................

Minimum Bending Radius: 6×OD

Maximum Conductor Operating Temperature: +90℃

»  Dimensions and Weight

........................................................................................

| Construction | No. of Strands | Grounding Conductor Size | Ground Check Conductor Size | Nominal Insulation Thickness |  | Nominal Jacket Thickness |  | Nominal Overall Diameter |  | Nominal Weight |  | Ampacity |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
| No. of cores×AWG/ kcmil | - | AWG/ kcmil | AWG/ kcmil | inch | mm | inch | mm | inch | mm | lbs/kft | kg/km | A |
| 3×6 | 133 | 10 | 10 | 0�07 | 1�8 | 0�155 | 3�9 | 1�29 | 32�8 | 1069 | 1590 | 93 |
| 3×4 | 259 | 8 | 10 | 0�07 | 1�8 | 0�155 | 3�9 | 1�40 | 35�6 | 1295 | 1927 | 122 |
| 3×2 | 259 | 6 | 10 | 0�07 | 1�8 | 0�170 | 4�3 | 1�59 | 40�4 | 1778 | 2645 | 159 |
| 3×1 | 259 | 5 | 8 | 0�08 | 2�0 | 0�190 | 4�8 | 1�76 | 44�7 | 2163 | 3218 | 184 |
| 3×1/0 | 266 | 4 | 8 | 0�08 | 2�0 | 0�190 | 4�8 | 1�86 | 47�2 | 2508 | 3731 | 211 |
| 3×2/0 | 323 | 3 | 8 | 0�08 | 2�0 | 0�205 | 5�2 | 2�00 | 50�8 | 3001 | 4465 | 243 |
| 3×3/0 | 418 | 2 | 8 | 0�08 | 2�0 | 0�205 | 5�2 | 2�13 | 54�1 | 3470 | 5163 | 279 |
| 3×4/0 | 532 | 1 | 8 | 0�08 | 2�0 | 0�220 | 5�6 | 2�31 | 58�7 | 4192 | 6237 | 321 |
| 3×250 | 627 | 1/0 | 6 | 0�095 | 2�4 | 0�220 | 5�6 | 2�51 | 63�8 | 5213 | 7756 | 355 |
| 3×350 | 888 | 2/0 | 6 | 0�095 | 2�4 | 0�235 | 6�0 | 2�81 | 71�4 | 6824 | 10153 | 435 |
| 3×500 | 1221 | 4/0 | 6 | 0�095 | 2�4 | 0�265 | 6�7 | 3�19 | 81�0 | 9014 | 13411 | 536 |

Ampacity-Based on a conductor temperature of 90℃ and an ambient air temperature of 40℃, per ICEA S-75-381�

40	www.caledonian-cables.co.uk  www.addison-cables.com

Caledonian Mining Cables

Portable Power Cables

Type SHD-GC Three-Conductor

Round Portable Power Cable, CPE Jacket 5kV

» Applications .............................................................................................................

These heavy duty cables are designed for applications such as longwall shearers, continuous miners and mobile equipment such as shovels, dredges and drills�

»  Standards

................................................................................................................

ICEA S-75-381/NEMA WC 58 ASTM B 172

ASTM B 33

CAN/CSA-C22�2 No�96

» Construction ............................................................................................................

Ground Check Conductor

Stranded Tinned Copper Conductor Conductor Shield

Grounding Conductor EPR Insulation Insulation Shield Reinforced CPE Jacket

Conductors:

Stranded annealed tinned copper conductor�

Conductor  Shield: Conducting layer� Insulation:

Ethylene Propylene Rubber (EPR)�

Insulation Shield:

Tinned copper/textile braid�

www.caledonian-cables.co.uk  www.addison-cables.com	41

Caledonian Mining Cables

Portable Power Cables

Ground Check Conductor:

Tinned copper with a yellow polypropylene insulation�

Grounding  Conductor: Tinned copper conductor� Jacket:

Reinforced extra-heavy-duty Chlorinated Polyethylene (CPE), black�

» Options .....................................................................................................................

- Other jacket materials such as CSP/PCP/NBR/PVC/TPU are available upon request�

- Two-layer jacket with reinforcing fibre between the two layers can be oﬀered  as an option�

»  Mechanical and Thermal Properties ......................................................................

Minimum Bending Radius: 6×OD

Maximum Conductor Operating Temperature: +90℃

»  Dimensions and Weight

........................................................................................

| Construction | No. of Strands | Grounding Conductor Size | Ground Check Conductor Size | Nominal Insulation Thickness |  | Nominal Jacket Thickness |  | Nominal Overall Diameter |  | Nominal Weight |  | Ampacity |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
| No. of cores×AWG/ kcmil | - | AWG/ kcmil | AWG/ kcmil | inch | mm | inch | mm | inch | mm | lbs/kft | kg/km | A |
| 3×6 | 133 | 10 | 8 | 0�110 | 2�8 | 0�185 | 4�7 | 1�56 | 39�6 | 1560 | 2322 | 93 |
| 3×4 | 259 | 8 | 8 | 0�110 | 2�8 | 0�185 | 4�7 | 1�68 | 42�7 | 1895 | 2820 | 122 |
| 3×2 | 259 | 6 | 8 | 0�110 | 2�8 | 0�205 | 5�2 | 1�87 | 47�5 | 2445 | 3639 | 159 |
| 3×1 | 259 | 5 | 8 | 0�110 | 2�8 | 0�205 | 5�2 | 1�95 | 49�5 | 2800 | 4167 | 184 |
| 3×1/0 | 266 | 4 | 8 | 0�110 | 2�8 | 0�220 | 5�6 | 2�08 | 52�8 | 3230 | 4807 | 211 |
| 3×2/0 | 329 | 3 | 8 | 0�110 | 2�8 | 0�220 | 5�6 | 2�20 | 55�9 | 3800 | 5655 | 243 |
| 3×3/0 | 418 | 2 | 8 | 0�110 | 2�8 | 0�235 | 6�0 | 2�36 | 59�9 | 4475 | 6660 | 279 |
| 3×4/0 | 532 | 1 | 8 | 0�110 | 2�8 | 0�235 | 6�0 | 2�50 | 63�5 | 5265 | 7835 | 321 |
| 3×250 | 627 | 1/0 | 6 | 0�120 | 3�0 | 0�250 | 6�4 | 2�69 | 68�3 | 6105 | 9085 | 355 |
| 3×300 | 741 | 1/0 | 6 | 0�120 | 3�0 | 0�250 | 6�4 | 2�81 | 71�4 | 6875 | 10231 | 398 |
| 3×350 | 888 | 2/0 | 6 | 0�120 | 3�0 | 0�265 | 6�7 | 2�95 | 74�9 | 7795 | 11600 | 435 |
| 3×500 | 1221 | 4/0 | 6 | 0�120 | 3�0 | 0�280 | 7�1 | 3�31 | 84�1 | 10415 | 15499 | 536 |

Ampacity-Based on a conductor temperature of 90℃ and an ambient air temperature of 40℃, per ICEA S-75-381�

42	www.caledonian-cables.co.uk  www.addison-cables.com