Caledonian Mining Cables

Portable Power Cables

Type SHD-GC Three-Conductor  Round Portable Power Cable, TPU Jacket 5kV

� Applications .............................................................................................................

These heavy duty cables are designed for heavy mobile equipment such as drag lines, shovels, dredges, drills and for power feeders�

�  Standards

................................................................................................................

ICEA S-75-381/NEMA WC 58 ASTM B 172

ASTM B 33

CAN/CSA C22�2 No� 96

� Construction ............................................................................................................

Ground Check Conductor

Stranded Tinned Copper Conductor Conductor Shield

Grounding Conductor EPR Insulation Insulation Shield  TPU Jacket

Conductors:

Stranded annealed tinned copper conductor�

Conductor  Shield: Conducting layer� Insulation:

Ethylene Propylene Rubber (EPR)�

Insulation Shield:

Tinned copper/textile braid�

www.caledonian-cables.co.uk  www.addison-cables.com	43

Caledonian Mining Cables

Portable Power Cables

Ground Check Conductor:

Tinned copper conductor with a yellow polypropylene insulation�

Grounding  Conductor: Tinned copper conductor� Jacket:

Thermoplastic Polyurethane (TPU) Jacket, black�

� Options .....................................................................................................................

Other jacket materials such as CPE/CSP/PCP/NBR/PVC are available upon request�

Two-layer jacket with reinforcing fibre between the two layers can be oﬀered  as an option�

�  Mechanical and Thermal Properties ......................................................................

Minimum Bending Radius: 6�OD

Maximum Conductor Operating Temperature: +90℃

�  Dimensions and Weight

........................................................................................

| Construction | No. of Strands | Grounding Conductor Size | Ground Check Conductor Size | Nominal Insulation Thickness | Nominal Jacket Thickness | Nominal Overall Diameter | Nominal Weight | Ampacity |
| --- | --- | --- | --- | --- | --- | --- | --- | --- |
| No. of cores�AWG/ kcmil | - | AWG/ kcmil | AWG/ kcmil | inch | mm | inch | mm | inch | mm | lbs/kft | kg/km | A |
| 3�6 | 133 | 10 | 8 | 0�110 | 2�8 | 0�185 | 4�7 | 1�56 | 39�6 | 1342 | 1997 | 93 |
| 3�4 | 259 | 8 | 8 | 0�110 | 2�8 | 0�185 | 4�7 | 1�68 | 42�7 | 1629 | 2424 | 122 |
| 3�2 | 259 | 6 | 8 | 0�110 | 2�8 | 0�205 | 5�2 | 1�87 | 47�5 | 2228 | 3315 | 159 |
| 3�1 | 259 | 5 | 8 | 0�110 | 2�8 | 0�205 | 5�2 | 1�95 | 49�5 | 2447 | 3641 | 184 |
| 3�1/0 | 266 | 4 | 8 | 0�110 | 2�8 | 0�220 | 5�6 | 2�08 | 52�8 | 2760 | 4106 | 211 |
| 3�2/0 | 323 | 3 | 8 | 0�110 | 2�8 | 0�220 | 5�6 | 2�20 | 55�9 | 3238 | 4818 | 243 |
| 3�3/0 | 418 | 2 | 8 | 0�110 | 2�8 | 0�235 | 6�0 | 2�36 | 59�9 | 3792 | 5642 | 279 |
| 3�4/0 | 532 | 1 | 8 | 0�110 | 2�8 | 0�235 | 6�0 | 2�50 | 63�5 | 4548 | 6767 | 321 |
| 3�250 | 627 | 1/0 | 6 | 0�120 | 3�0 | 0�250 | 6�4 | 2�69 | 68�3 | 5427 | 8074 | 355 |
| 3�350 | 888 | 2/0 | 6 | 0�120 | 3�0 | 0�265 | 6�7 | 2�95 | 74�9 | 7070 | 10519 | 435 |
| 3�500 | 1221 | 4/0 | 6 | 0�120 | 3�0 | 0�280 | 7�1 | 3�31 | 84�1 | 9407 | 13996 | 536 |

Ampacity-Based on a conductor temperature of 90℃ and an ambient air temperature of 40℃, per ICEA S-75-381�

44	www.caledonian-cables.co.uk  www.addison-cables.com