Caledonian Mining Cables

Portable Power Cables

Type SHD-GC Three-Conductor

Round Portable Power Cable, TPU Jacket 15kV

» Applications .............................................................................................................

These heavy duty cables are designed for heavy mobile equipment such as drag lines, shovels, dredges, drills and for power feeders�

»  Standards

................................................................................................................

ICEA S-75-381/NEMA WC 58 ASTM B 172

ASTM B 33

CAN/CSA C22�2 No� 96

» Construction ............................................................................................................

Ground Check Conductor

Stranded Tinned Copper Conductor Conductor Shield

Grounding Conductor EPR Insulation Insulation Shield  TPU Jacket

Conductors:

Stranded annealed tinned copper conductor�

Conductor  Shield: Conducting layer� Insulation:

Ethylene Propylene Rubber (EPR)�

Insulation Shield:

Conducting tape + Tinned copper/textile braid�

www.caledonian-cables.co.uk  www.addison-cables.com	51

Caledonian Mining Cables

Portable Power Cables

Ground Check Conductor:

Tinned copper conductor with a yellow polypropylene insulation�

Grounding  Conductor: Tinned copper conductor� Jacket:

Thermoplastic Polyurethane (TPU) Jacket, black�

» Options .....................................................................................................................

- Other jacket materials such as CPE/CSP/PCP/NBR/PVC are available upon request�

- Two-layer jacket with reinforcing fibre between the two layers can be oﬀered  as an option�

»  Mechanical and Thermal Properties ......................................................................

Minimum Bending Radius: 8×OD

Maximum Conductor Operating Temperature: +90℃

»  Dimensions and Weight

........................................................................................

| Construction | No. of Strands | Grounding Conductor Size | Ground Check Conductor Size | Nominal Insulation Thickness |  | Nominal Jacket Thickness |  | Nominal Overall Diameter |  | Nominal Weight |  | Ampacity |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
| No. of cores×AWG/ kcmil | - | AWG/ kcmil | AWG/ kcmil | inch | mm | inch | mm | inch | mm | lbs/kft | kg/km | A |
| 3×2 | 259 | 6 | 8 | 0�210 | 5�3 | 0�235 | 6�0 | 2�41 | 61�2 | 3145 | 4679 | 164 |
| 3×1 | 259 | 5 | 8 | 0�210 | 5�3 | 0�235 | 6�0 | 2�52 | 64�0 | 3567 | 5307 | 187 |
| 3×1/0 | 266 | 4 | 8 | 0�210 | 5�3 | 0�250 | 6�4 | 2�64 | 67�0 | 3976 | 5916 | 215 |
| 3×2/0 | 323 | 3 | 8 | 0�210 | 5�3 | 0�250 | 6�4 | 2�73 | 69�3 | 4526 | 6734 | 246 |
| 3×3/0 | 418 | 2 | 8 | 0�210 | 5�3 | 0�265 | 6�7 | 2�90 | 73�7 | 5231 | 7783 | 283 |
| 3×4/0 | 532 | 1 | 8 | 0�210 | 5�3 | 0�265 | 6�7 | 3�05 | 77�5 | 6033 | 8976 | 325 |

Ampacity-Based on a conductor temperature of 90℃ and an ambient air temperature of 40℃, per ICEA S-75-381�

52	www.caledonian-cables.co.uk  www.addison-cables.com