Caledonian Mining Cables

Portable Power Cables

Type SHD-GC Three-Conductor

Round Portable Power Cable, TPU Jacket 25kV

� Applications .............................................................................................................

These heavy duty cables are designed for heavy mobile equipment such as drag lines, shovels, dredges, drills and for power feeders�

�  Standards

................................................................................................................

ICEA S-75-381/NEMA WC 58 ASTM B 172

ASTM B 33

CAN/CSA C22�2 No� 96

� Construction ............................................................................................................

Ground Check Conductor

Stranded Tinned Copper Conductor Conductor Shield

Grounding Conductor EPR Insulation Insulation Shield  TPU Jacket

Conductors:

Stranded annealed tinned copper conductor�

Conductor  Shield: Conducting layer� Insulation:

Ethylene Propylene Rubber (EPR)�

Insulation Shield:

Conducting tape + Tinned copper/textile braid�

www.caledonian-cables.co.uk  www.addison-cables.com	55

Caledonian Mining Cables

Portable Power Cables

Ground Check Conductor:

Tinned copper conductor with a yellow polypropylene insulation�

Grounding  Conductor: Tinned copper conductor� Jacket:

Thermoplastic Polyurethane (TPU) Jacket, black�

� Options .....................................................................................................................

Other jacket materials such as CPE/CSP/PCP/NBR/PVC are available upon request�

Two-layer jacket with reinforcing fibre between the two layers can be oﬀered  as an option�

�  Mechanical and Thermal Properties ......................................................................

Minimum Bending Radius: 8�OD

Maximum Conductor Operating Temperature: +90℃

�  Dimensions and Weight

........................................................................................

Caledonian Mining Cables

Portable Welding Cables

56	www.caledonian-cables.co.uk  www.addison-cables.com

| Construction | No. of Strands | Grounding Conductor Size | Ground Check Conductor Size | Nominal Insulation Thickness | Nominal Jacket Thickness | Nominal Overall Diameter | Nominal Weight | Ampacity |
| --- | --- | --- | --- | --- | --- | --- | --- | --- |
| No. of cores�AWG/ kcmil | - | AWG/ kcmil | AWG/ kcmil | inch | mm | inch | mm | inch | mm | lbs/kft | kg/km | A |
| 3�1 | 259 | 5 | 8 | 0�260 | 6�6 | 0�265 | 6�7 | 2�95 | 74�9 | 4410 | 6561 | 191 |
| 3�1/0 | 266 | 4 | 8 | 0�260 | 6�6 | 0�265 | 6�7 | 3�05 | 77�5 | 4866 | 7240 | 218 |
| 3�2/0 | 323 | 3 | 8 | 0�260 | 6�6 | 0�280 | 7�1 | 3�20 | 81�3 | 5560 | 8272 | 249 |
| 3�3/0 | 418 | 2 | 8 | 0�260 | 6�6 | 0�280 | 7�1 | 3�33 | 84�6 | 6192 | 9213 | 286 |
| 3�4/0 | 532 | 1 | 8 | 0�260 | 6�6 | 0�295 | 7�5 | 3�50 | 88�9 | 7110 | 10578 | 327 |

Ampacity-Based on a conductor temperature of 90℃ and an ambient air temperature of 40℃, per ICEA S-75-381�

56	www.caledonian-cables.co.uk  www.addison-cables.com