Caledonian Mining Cables

Mine Power Feeder Cables

Type MP-GC Three-Conductor

Mine Power Feeder Cable, CPE Jacket, 5kV

� Applications .............................................................................................................

These cables are designed for connections between units of mine distribution systems, suitable for installed in duct, conduit or open air and for direct burial in wet and dry locations�

�  Standarhads

............................................................................................................

ICEA S-75-381/NEMA WC 58 ASTM B-8

CAN/CSA-C22�2 No�96

� Construction ............................................................................................................

Ground Check Conductor Stranded Bare Copper Conductor Conductor Shield

Grounding Conductor EPR Insulation Insulation Shield CPE Jacket

Conductors:

Stranded annealed bare copper conductor�

Conductor  Shield: Conducting layer� Insulation:

Ethylene Propylene Rubber (EPR)�

Insulation  Shield: Conducting layer + copper tape� Ground  Check  Conductor:

Copper conductor with a yellow polypropylene insulation�

www.caledonian-cables.co.uk  www.addison-cables.com	59

Caledonian Mining Cables

Mine Power Feeder Cables

Grounding  Conductor: Tinned copper conductor� Jacket:

Chlorinated Polyethylene (CPE), black�

� Options .....................................................................................................................

Other jacket materials such as CSP/PCP/NBR/PVC/TPU are available upon request�

�  Mechanical and Thermal Properties ......................................................................

Minimum Bending Radius: 12�OD

Maximum Conductor Operating Temperature: +90℃

�  Dimensions and Weight

........................................................................................

| Construction | No. of Strands | Grounding Conductor Size | Ground Check Conductor Size | Nominal Insulation Thickness | Nominal Jacket Thickness | Nominal Overall Diameter | Nominal Weight | Ampacity |
| --- | --- | --- | --- | --- | --- | --- | --- | --- |
| No. of cores�AWG/ kcmil | - | AWG/ kcmil | AWG/ kcmil | inch | mm | inch | mm | inch | mm | lbs/kft | kg/km | A |
| 3�6 | 7 | 10 | 8 | 0�09 | 2�3 | 0�11 | 2�8 | 1�30 | 33�0 | 1060 | 1577 | 93 |
| 3�4 | 7 | 8 | 8 | 0�09 | 2�3 | 0�11 | 2�8 | 1�41 | 35�8 | 1441 | 2144 | 122 |
| 3�2 | 7 | 6 | 8 | 0�09 | 2�3 | 0�11 | 2�8 | 1�47 | 37�3 | 1827 | 2718 | 159 |
| 3�1 | 19 | 5 | 8 | 0�09 | 2�3 | 0�11 | 2�8 | 1�54 | 39�1 | 2168 | 3226 | 184 |
| 3�1/0 | 19 | 4 | 8 | 0�09 | 2�3 | 0�11 | 2�8 | 1�63 | 41�4 | 2602 | 3871 | 211 |
| 3�2/0 | 19 | 3 | 8 | 0�09 | 2�3 | 0�11 | 2�8 | 1�72 | 43�7 | 3010 | 4478 | 243 |
| 3�3/0 | 19 | 2 | 8 | 0�09 | 2�3 | 0�14 | 3�6 | 1�89 | 48�0 | 3265 | 4859 | 279 |
| 3�4/0 | 19 | 1 | 8 | 0�09 | 2�3 | 0�14 | 3�6 | 2�01 | 51�0 | 4190 | 6234 | 321 |
| 3�250 | 37 | 1/0 | 8 | 0�09 | 2�3 | 0�14 | 3�6 | 2�10 | 53�3 | 4825 | 7179 | 355 |
| 3�350 | 37 | 2/0 | 8 | 0�09 | 2�3 | 0�14 | 3�6 | 2�31 | 58�7 | 6062 | 9019 | 435 |
| 3�500 | 37 | 4/0 | 8 | 0�09 | 2�3 | 0�14 | 3�6 | 2�59 | 65�8 | 8427 | 12538 | 536 |

Ampacity-Based on a conductor temperature of 90℃ and an ambient air temperature of 40℃, per ICEA S-75-381�

60	www.caledonian-cables.co.uk  www.addison-cables.com