Caledonian Mining Cables

Mine Power Feeder Cables

Type MP-GC Three-Conductor

Mine Power Feeder Cable, CPE Jacket, 25kV

» Applications .............................................................................................................

These cables are designed for connections between units of mine distribution systems, suitable for installed in duct, conduit or open air and for direct burial in wet and dry locations�

»  Standards

................................................................................................................

ICEA S-75-381/NEMA WC 58 ASTM B-8

CAN/CSA-C22�2 No�96

» Construction ............................................................................................................

Ground Check Conductor Stranded Bare Copper Conductor Conductor Shield

Grounding Conductor EPR Insulation Insulation Shield CPE Jacket

Conductors:

Stranded annealed bare copper conductor�

Conductor  Shield: Conducting layer� Insulation:

Ethylene Propylene Rubber (EPR)�

Insulation  Shield: Conducting layer + copper tape� Ground  Check  Conductor:

Copper conductor with a yellow polypropylene insulation�

www.caledonian-cables.co.uk  www.addison-cables.com	65

Caledonian Mining Cables

Mine Power Feeder Cables

Grounding  Conductor: Tinned copper conductor� Jacket:

Chlorinated Polyethylene (CPE), black�

» Options .....................................................................................................................

- Other jacket materials such as CSP/PCP/NBR/PVC/TPU are available upon request�

»  Mechanical and Thermal Properties ......................................................................

Minimum Bending Radius: 12×OD

Maximum Conductor Operating Temperature: +90℃

»  Dimensions and Weight

........................................................................................

| Construction | No. of Strands | Grounding Conductor Size | Ground Check Conductor Size | Nominal Insulation Thickness |  | Nominal Jacket Thickness |  | Nominal Overall Diameter |  | Nominal Weight |  | Ampacity |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
| No. of cores×AWG/ kcmil | - | AWG/ kcmil | AWG/kcmil | inch | mm | inch | mm | inch | mm | lbs/kft | kg/km | A |
| 3×1 | 19 | 5 | 8 | 0�260 | 6�4 | 0�14 | 3�6 | 2�37 | 60�2 | 3435 | 5112 | 187 |
| 3×1/0 | 19 | 4 | 8 | 0�260 | 6�4 | 0�14 | 3�6 | 2�45 | 62�2 | 3815 | 5677 | 218 |
| 3×2/0 | 19 | 3 | 8 | 0�260 | 6�4 | 0�14 | 3�6 | 2�54 | 64�5 | 4290 | 6384 | 249 |
| 3×3/0 | 19 | 2 | 8 | 0�260 | 6�4 | 0�14 | 3�6 | 2�65 | 67�3 | 4875 | 7255 | 286 |
| 3×4/0 | 19 | 1 | 8 | 0�260 | 6�4 | 0�14 | 3�6 | 2�81 | 71�4 | 5665 | 8430 | 327 |
| 3×250 | 37 | 1/0 | 8 | 0�260 | 6�4 | 0�17 | 4�3 | 2�97 | 75�4 | 6495 | 9666 | 360 |
| 3×350 | 37 | 2/0 | 8 | 0�260 | 6�4 | 0�17 | 4�3 | 3�18 | 80�8 | 7970 | 11860 | 438 |
| 3×500 | 37 | 4/0 | 8 | 0�260 | 6�4 | 0�17 | 4�3 | 3�45 | 87�6 | 10300 | 15328 | 536 |

Ampacity-Based on a conductor temperature of 90℃ and an ambient air temperature of 40℃, per ICEA S-75-381�

66	www.caledonian-cables.co.uk  www.addison-cables.com