Caledonian Mining Cables

Mine Power Feeder Cables

Type MP-GC Three-Conductor

Mine Power Feeder Cable, PVC Jacket, 5kV

» Applications .............................................................................................................

These cables are designed for connections between units of mine distribution systems, suitable for direct burial in wet and dry locations�

»  Standards

................................................................................................................

ICEA S-75-381/NEMA WC 58 ASTM B-8

CAN/CSA C22�2 No� 96

» Construction ............................................................................................................

Ground Check Conductor Stranded Bare Copper Conductor Conductor Shield

Grounding Conductor XLPE Insulation Insulation Shield PVC Jacket

Conductors:

Stranded annealed bare copper conductor�

Conductor  Shield: Conducting layer� Insulation:

Cross-Linked Polyethylene (XLPE)�

Insulation  Shield: Conducting layer + copper tape� Ground  Check  Conductor:

Copper conductor with a yellow polypropylene insulation�

www.caledonian-cables.co.uk  www.addison-cables.com	67

Caledonian Mining Cables

Mine Power Feeder Cables

Grounding  Conductor: Tinned copper conductor� Jacket:

Polyvinyl Chloride (PVC), black�

» Options .....................................................................................................................

- Other jacket materials such as CSP/PCP/NBR/CPE/TPU are available upon request�

»  Mechanical and Thermal Properties ......................................................................

Minimum Bending Radius: 12×OD

Maximum Conductor Operating Temperature: +90℃

»  Dimensions and Weight

........................................................................................

| Construction | No. of Strands | Grounding Conductor Size | Ground Check Conductor Size | Nominal Insulation Thickness |  | Nominal Jacket Thickness |  | Nominal Overall Diameter |  | Nominal Weight |  | Ampacity |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
| No. of cores×AWG/ kcmil | - | AWG/ kcmil | AWG/ kcmil | inch | mm | inch | mm | inch | mm | lbs/kft | kg/km | A |
| 3×4 | 7 | 8 | 8 | 0�09 | 2�3 | 0�11 | 2�8 | 1�41 | 35�8 | 1224 | 1821 | 122 |
| 3×2 | 7 | 6 | 8 | 0�09 | 2�3 | 0�11 | 2�8 | 1�47 | 37�3 | 1653 | 2459 | 159 |
| 3×1 | 19 | 5 | 8 | 0�09 | 2�3 | 0�11 | 2�8 | 1�54 | 39�1 | 1950 | 2901 | 184 |
| 3×1/0 | 19 | 4 | 8 | 0�09 | 2�3 | 0�11 | 2�8 | 1�63 | 41�4 | 2200 | 3273 | 211 |
| 3×2/0 | 19 | 3 | 8 | 0�09 | 2�3 | 0�11 | 2�8 | 1�72 | 43�7 | 2721 | 4048 | 243 |
| 3×3/0 | 19 | 2 | 8 | 0�09 | 2�3 | 0�14 | 3�6 | 1�89 | 48�0 | 3170 | 4720 | 279 |
| 3×4/0 | 19 | 1 | 8 | 0�09 | 2�3 | 0�14 | 3�6 | 2�01 | 51�0 | 3845 | 5721 | 321 |
| 3×250 | 37 | 1/0 | 8 | 0�09 | 2�3 | 0�14 | 3�6 | 2�10 | 53�3 | 4321 | 6429 | 355 |
| 3×350 | 37 | 2/0 | 8 | 0�09 | 2�3 | 0�14 | 3�6 | 2�31 | 58�7 | 5652 | 8409 | 435 |
| 3×500 | 37 | 4/0 | 8 | 0�09 | 2�3 | 0�14 | 3�6 | 2�59 | 65�8 | 7721 | 11487 | 536 |

Ampacity-Based on a conductor temperature of 90℃ and an ambient air temperature of 40℃, per ICEA S-75-381�

68	www.caledonian-cables.co.uk  www.addison-cables.com