Caledonian Mining Cables

Mine Power Feeder Cables

Type MP-GC Three-Conductor

Mine Power Feeder Cable, PVC Jacket, 8kV

» Applications .............................................................................................................

These cables are designed for connections between units of mine distribution systems, suitable for installed in duct, conduit or open air and for direct burial in wet and dry locations�

»  Standards

................................................................................................................

ICEA S-75-381/NEMA WC 58 ASTM B-8

CAN/CSA-C22�2 No�96

» Construction ............................................................................................................

Ground Check Conductor Stranded Bare Copper Conductor Conductor Shield

Grounding Conductor XLPE Insulation Insulation Shield PVC Jacket

Conductors:

Stranded annealed bare copper conductor�

Conductor  Shield: Conducting layer� Insulation:

Cross-Linked Polyethylene (XLPE)�

Insulation  Shield: Conducting layer + copper tape� Ground  Check  Conductor:

Copper conductor with a yellow polypropylene insulation�

www.caledonian-cables.co.uk  www.addison-cables.com	69

Caledonian Mining Cables

Mine Power Feeder Cables

Grounding  Conductor: Tinned copper conductor� Jacket:

Polyvinyl Chloride (PVC), black�

» Options .....................................................................................................................

- Other jacket materials such as CSP/PCP/NBR/CPE/TPU are available upon request�

»  Mechanical and Thermal Properties ......................................................................

Minimum Bending Radius: 12×OD

Maximum Conductor Operating Temperature: +90℃

»  Dimensions and Weight

........................................................................................

| Construction | No. of Strands | Grounding Conductor Size | Ground Check Conductor Size | Nominal Insulation Thickness |  | Nominal Jacket Thickness |  | Nominal Overall Diameter |  | Nominal Weight |  | Ampacity |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
| No. of cores×AWG/ kcmil | - | AWG/ kcmil | AWG/ kcmil | inch | mm | inch | mm | inch | mm | lbs/kft | kg/km | A |
| 3×4 | 7 | 8 | 8 | 0�115 | 2�9 | 0�11 | 2�8 | 1�52 | 38�6 | 1366 | 2032 | 122 |
| 3×2 | 7 | 6 | 8 | 0�115 | 2�9 | 0�11 | 2�8 | 1�58 | 40�1 | 1727 | 2569 | 159 |
| 3×1 | 19 | 5 | 8 | 0�115 | 2�9 | 0�11 | 2�8 | 1�66 | 42�2 | 2174 | 3234 | 184 |
| 3×1/0 | 19 | 4 | 8 | 0�115 | 2�9 | 0�11 | 2�8 | 1�74 | 44�2 | 2656 | 3952 | 211 |
| 3×2/0 | 19 | 3 | 8 | 0�115 | 2�9 | 0�14 | 3�6 | 1�90 | 48�3 | 2895 | 4307 | 243 |
| 3×3/0 | 19 | 2 | 8 | 0�115 | 2�9 | 0�14 | 3�6 | 2�00 | 50�8 | 3320 | 4950 | 279 |
| 3×4/0 | 19 | 1 | 8 | 0�115 | 2�9 | 0�14 | 3�6 | 2�12 | 53�8 | 3983 | 5926 | 321 |
| 3×250 | 37 | 1/0 | 8 | 0�115 | 2�9 | 0�14 | 3�6 | 2�22 | 56�4 | 4484 | 6671 | 355 |
| 3×350 | 37 | 2/0 | 8 | 0�115 | 2�9 | 0�14 | 3�6 | 2�43 | 61�7 | 5827 | 8669 | 435 |
| 3×500 | 37 | 4/0 | 8 | 0�115 | 2�9 | 0�14 | 3�6 | 2�70 | 68�6 | 7893 | 11743 | 536 |

Ampacity-Based on a conductor temperature of 90℃ and an ambient air temperature of 40℃, per ICEA S-75-381�

70	www.caledonian-cables.co.uk  www.addison-cables.com