Caledonian Mining Cables

Mine Power Feeder Cables

Type MP-GC Three-Conductor

Mine Power Feeder Cable, PVC Jacket, 15kV

» Applications .............................................................................................................

These cables are designed for connections between units of mine distribution systems, suitable for installed in duct, conduit or open air and for direct burial in wet and dry locations�

»  Standards

................................................................................................................

ICEA S-75-381/NEMA WC 58 ASTM B-8

CAN/CSA-C22�2 No�96

» Construction ............................................................................................................

Ground Check Conductor Stranded Bare Copper Conductor Conductor Shield

Grounding Conductor XLPE Insulation Insulation Shield PVC Jacket

Conductors:

Stranded annealed bare copper conductor�

Conductor  Shield: Conducting layer� Insulation:

Cross-Linked Polyethylene (XLPE)�

Insulation  Shield: Conducting layer + copper tape� Ground  Check  Conductor:

Copper conductor with a yellow polypropylene insulation�

www.caledonian-cables.co.uk  www.addison-cables.com	71

Caledonian Mining Cables

Mine Power Feeder Cables

Grounding  Conductor: Tinned copper conductor� Jacket:

Polyvinyl Chloride (PVC), black�

» Options .....................................................................................................................

- Other jacket materials such as CSP/PCP/NBR/CPE/TPU are available upon request�

»  Mechanical and Thermal Properties ......................................................................

Minimum Bending Radius: 12×OD

Maximum Conductor Operating Temperature: +90℃

»  Dimensions and Weight

........................................................................................

| Construction | No. of Strands | Grounding Conductor Size | Ground Check Conductor Size | Nominal Insulation Thickness |  | Nominal Jacket Thickness |  | Nominal Overall Diameter |  | Nominal Weight |  | Ampacity |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
| No. of cores×AWG/ kcmil | - | AWG/ kcmil | AWG/ kcmil | inch | mm | inch | mm | inch | mm | lbs/kft | kg/km | A |
| 3×2 | 7 | 6 | 8 | 0�175 | 4�4 | 0�14 | 3�6 | 1�90 | 48�3 | 2021 | 3007 | 164 |
| 3×1 | 19 | 5 | 8 | 0�175 | 4�4 | 0�14 | 3�6 | 1�99 | 50�6 | 2503 | 3724 | 187 |
| 3×1/0 | 19 | 4 | 8 | 0�175 | 4�4 | 0�14 | 3�6 | 2�07 | 52�6 | 2658 | 3955 | 215 |
| 3×2/0 | 19 | 3 | 8 | 0�175 | 4�4 | 0�14 | 3�6 | 2�16 | 54�9 | 3066 | 4562 | 246 |
| 3×3/0 | 19 | 2 | 8 | 0�175 | 4�4 | 0�14 | 3�6 | 2�27 | 57�7 | 3710 | 5530 | 283 |
| 3×4/0 | 19 | 1 | 8 | 0�175 | 4�4 | 0�14 | 3�6 | 2�39 | 60�7 | 4369 | 6500 | 325 |
| 3×250 | 37 | 1/0 | 8 | 0�175 | 4�4 | 0�14 | 3�6 | 2�48 | 63�0 | 4875 | 7253 | 359 |
| 3×350 | 37 | 2/0 | 8 | 0�175 | 4�4 | 0�14 | 3�6 | 2�70 | 68�6 | 6412 | 9540 | 438 |
| 3×500 | 37 | 4/0 | 8 | 0�175 | 4�4 | 0�17 | 4�3 | 3�08 | 78�2 | 8610 | 12810 | 536 |

Ampacity-Based on a conductor temperature of 90℃ and an ambient air temperature of 40℃, per ICEA S-75-381�

72	www.caledonian-cables.co.uk  www.addison-cables.com