Caledonian Mining Cables

Portable Power Cables

Type W Three-Conductor Round Portable Power Cable 2kV

» Applications .............................................................................................................

These cables are designed for general use where bare grounding conductors are not required or desired�

» Standards .................................................................................................................

ICEA S-75-381/NEMA WC 58 ASTM B 172

ASTM B 33

CAN/CSA C22�2 No� 96

» Construction ............................................................................................................

Stranded Tinned Copper Conductor

EPR Insulation

Reinforced CPE Jacket

Conductors:

Stranded annealed tinned copper conductor�

Insulation:

Ethylene Propylene Rubber (EPR)�

Jacket:

Reinforced heavy-duty/extra-heavy-duty Chlorinated Polyethylene (CPE), black� (Cables having a nominal outside diameter of more than 2�0 inches require extra-heavy-duty jackets�)

» Options .....................................................................................................................

- Other jacket materials such as CSP/PCP/NBR/PVC are available upon request�

- Two-layer jacket with reinforcing fibre between the two layers can be oﬀered  as an option�

www.caledonian-cables.co.uk  www.addison-cables.com	7

Caledonian Mining Cables

Portable Power Cables

»  Mechanical and Thermal Properties ......................................................................

Minimum Bending Radius: 6×OD

Maximum Conductor Operating Temperature: +90℃

»  Dimensions and Weight ..........................................................................................

| Construction | No. of Strands | Nominal Insulation Thickness |  | Nominal Jacket Thickness |  | Nominal Overall Diameter |  | Nominal Weight |  | Ampacity |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
| No. of cores×AWG/ kcmil | - | inch | mm | inch | mm | inch | mm | lbs/kft | kg/km | A |
| 3×8 | 133 | 0�06 | 1�5 | 0�125 | 3�2 | 0�91 | 23�1 | 550 | 818 | 59 |
| 3×6 | 133 | 0�06 | 1�5 | 0�140 | 3�6 | 1�01 | 25�7 | 730 | 1086 | 79 |
| 3×4 | 259 | 0�06 | 1�5 | 0�155 | 3�9 | 1�17 | 29�7 | 1020 | 1518 | 104 |
| 3×2 | 259 | 0�06 | 1�5 | 0�155 | 3�9 | 1�34 | 34�0 | 1430 | 2128 | 138 |
| 3×1 | 259 | 0�08 | 2�0 | 0�170 | 4�3 | 1�51 | 38�4 | 1800 | 2678 | 161 |
| 3×1/0 | 266 | 0�08 | 2�0 | 0�170 | 4�3 | 1�65 | 41�9 | 2140 | 3184 | 186 |
| 3×2/0 | 342 | 0�08 | 2�0 | 0�190 | 4�8 | 1�75 | 44�5 | 2580 | 3839 | 215 |
| 3×3/0 | 418 | 0�08 | 2�0 | 0�190 | 4�8 | 1�89 | 48�0 | 2922 | 4347 | 249 |
| 3×4/0 | 532 | 0�08 | 2�0 | 0�205 | 5�2 | 2�04 | 51�8 | 3800 | 5654 | 287 |
| 3×250 | 741 | 0�095 | 2�4 | 0�220 | 5�6 | 2�39 | 60�7 | 4368 | 6500 | 320 |
| 3×350 | 888 | 0�095 | 2�4 | 0�235 | 6�0 | 2�66 | 67�5 | 5895 | 8772 | 394 |
| 3×500 | 1221 | 0�095 | 2�4 | 0�250 | 6�4 | 2�98 | 75�8 | 7820 | 11638 | 487 |

Ampacity-Based on a conductor temperature of 90℃ and an ambient air temperature of 40℃, per ICEA S-75-381�

8	www.caledonian-cables.co.uk  www.addison-cables.com