Materials Requirements According to ICEA S-75-381

»  Table 1 Power Conductor Insulation Requirements.............................................

The insulation for the power conductor shall meet the requirements given in the table below�

|  | Ethylene Propylene |  |  |  | Crosslinked Polyethylene |  |
| --- | --- | --- | --- | --- | --- | --- |
|  | Type I |  | Type II |  |  |  |
|  | Up to 2 kV | Above 2 kV | Up to 2 kV | Above 2 kV | Up to 2 kV | Above 2 kV |
| 1.INITIAL PHYSICAL PROPERTIES |  |  |  |  |  |  |
| Tensile strength, minimum, psi | 700 | 700 | 1200 | 1200 | 1800 | 1800 |
| Tensile stress@100% |  |  |  |  |  |  |
| Elongation, minimum, psi | - | - | 500 | 500 | - | - |
| Elongation at rupture, minimum,% | 250 | 250 | 150 | 150 | 250 | 250 |
| 2.AIR OVEN AGING (After Conditioning@121℃ +/- 1℃ for 168 hours) |  |  |  |  |  |  |
| Tensile strength & elongation minimum, percentage of unaged value | 75 | 75 | 75 | 75 | 75 | 75 |
| 3.ACCELERATED WATER ABSORPTION |  |  |  |  |  |  |
| Dielectric constant after 24 hours, maximum | 6�0 | 4�0 | 6�0 | 4�0 | 6�0 | 3�5 |
| Increase in capacitance maximum, percent |  |  |  |  |  |  |
| 1-14 days | 5�0 | 3�5 | 5�0 | 3�5 | 3�0 | 3�0 |
| 7-14 days | 3�0 | 1�5 | 3�0 | 1�5 | 1�5 | 1�5 |
| *Stab. factor after 14 days or | 1�0 | 1�0 | 1�0 | 1�0 | 1�0 | 1�0 |
| *Alternate to Stability Factor (Stability Factor Difference) 1-14 days max. | 0�5 | 0�5 | 0�5 | 0�5 | 0�5 | 0�5 |
| 4.INSULATION RESISTANCE |  |  |  |  |  |  |

|  | Ethylene Propylene |  |  |  | Crosslinked Polyethylene |  |
| --- | --- | --- | --- | --- | --- | --- |
|  | Type I |  | Type II |  |  |  |
|  | Up to 2 kV | Above 2 kV | Up to 2 kV | Above 2 kV | Up to 2 kV | Above 2 kV |
| IR@15.6℃, minimum, Megohms-1000ft | 10,000 | 20,000 | 10,000 | 20,000 | 10,000 | 20,000 |
| 5.ADDITIONAL REQUIREMENTS |  |  |  |  |  |  |
| Power factor maximum, % after 24 hr | - | 2�0 | - | 2�0 | - | 2�0 |
| **Permittivity (SIC) | - | 4�0 | - | 4�0 | - | 3�5 |
| Hot creep (ICEA T-28-562) (After conditioning@150℃+/-2℃) |  |  |  |  | All Voltages |  |
|  |  |  |  |  | ***Unfilled | ***Filled |
| Elongation, maximum % | 50 | 50 | 50 | 50 | 175 | 100 |
| Set, maximum, % | 5 | 5 | 5 | 5 | 10 | 5 |

* Only one of these two requirements needs to be satisfied, not both�

**Applies only to cables rated 5,001 volts and above�

***If this value is exceeded, the solvent extraction test may be performed and will serve as a referee method to determine compliance� Requirement shall be 30 percent maximum extractibles after 20 hours drying�

»  Table 2 Ground Check Conductor & Control Conductor Insulation

Requirements      ...............................................................................................................

The insulation for the ground-check and control conductors shall be one of the types given in the table below and shall meet the requirements specified in it�

|  | Crosslinked |  |  |  |  | Thermoplastic |  |
| --- | --- | --- | --- | --- | --- | --- | --- |
|  | Ethylene Propylene |  | Crosslinked Polyethylene | Chlorinated Polyethylene | Chlorosulfonated Polyethylene | Thermoplastic Elastomer | Polypropylene |
|  | Type I | Type II |  |  |  |  |  |
| 1.INITIAL PHYSICAL PROPERTIES (At Room Temperature) |  |  |  |  |  |  |  |
| Tensile strength, minimum, psi | 700 | 1200 | 1800 | 1500 | 1500 | 1500 | 3000 |
| Tensile stress@100% |  |  |  |  |  |  |  |
| Elongation, minimum, psi | - | 500 | - | - | - | - | 2500 |
| Elongation at rupture, minimum, percent | 250 | 150 | 250 | 300 | 300 | 300 | 300 |
| Set, maximum, percent | - | - |  | 30 | 30 |  |  |
| 2.AIR OVEN AGING REQUIREMENTS |  |  |  |  |  |  |  |
| After conditioning@℃ +/- 1℃ | 121 | 121 | 121 | 121 | 121 | 121 | 100 |
| Hours | 168 | 168 | 168 | 168 | 168 | 168 | 48 |
| Minimum percent retention of original value |  |  |  |  |  |  |  |
| Tensile strength | 75 | 75 | 75 | 85 | 85 | 75 | 75 |
| Elongation | 75 | 75 | 75 | 55 | 50 | 75 | 75 |

»  Table 3 Extra-Heavy-Duty Crosslinked Jackets and Thermoplastic

Polyurethane.................................................................................................................

The jacket for portable cables shall meet the appropriate requirements in Table 3 and 4

|  | Chlorinated Polyethylene (CPE) | Neoprene (PCP) | Nitrile Butadiene (NBR)/ Polyvinyl Chloride (PVC) | Chlorosulfonated Polyethylene* (CSP/CSPE) | Thermoplastic Polyurethane (TPU) |
| --- | --- | --- | --- | --- | --- |
| 1. PHYSICAL PROPERTIES |  |  |  |  |  |
| Tensile strength, minimum, psi | 2400 | 2400 | 2400 | 2400 | 3700 |
| Tensile stress at 200 percent elongation, minimum, psi | 700 | 700 | 700 | 700 | 800 |
| Elongation at rupture, minimum, percent | 300 | 300 | 300 | 300 | 400 |
| Set, maximum, percent | 30 | 20 | 30 | 30 | N/A |
| Tear resistance, minimum, ppi | 40 | 40 | 40 | 40 | 80 |
| 2.AGING REQUIREMENTS (After air oven test at 100℃ +/- 1℃ for 168 hours) |  |  |  |  |  |
| Tensile strength, minimum, percentage of unaged value | 70 | 50 | 50 | 70 | 50 |
| Elongation at rupture, minimum, percentage of unaged value | 55 | 50 | 50 | 60 | 75 |
| 3.AGING REQUIREMENTS (After oil immersion test at 121℃+/-1℃ for 18 hours) |  |  |  |  |  |
| Tensile strength and elongation, minimum, percentage of unaged value | 60 | 60 | 60 | 60 | 60 |
| 4.ELECTRICAL REQUIREMENTS |  |  |  |  |  |
| Surface resistance,nonshielded cables minimum, megohms | 100 | 100 | 100 | 100 | N/A |

*Also known as Chlorosulfonyl Polyethylene

»  Table 4 Heavy-Duty Crosslinked Jackets ..............................................................

The jacket for portable cables shall meet the appropriate requirements in Table 3 and 4�

The jacket for mine power feeder cables shall be a crosslinked jacket meets the requirements of Table 4 or a thermoplastic jacket that meets the requirements of Table 5�

|  | Chlorinated Polyethylene (CPE) | Neoprene (PCP) | Nitrile Butadiene (NBR)/ Polyvinyl Chloride (PVC) | Chlorosulfonated Polyethylene* (CSP/ CSPE) |
| --- | --- | --- | --- | --- |
| 1. PHYSICAL REQUIREMENTS |  |  |  |  |
| Tensile strength, minimum, psi | 1800 | 1800 | 1800 | 1800 |
| Tensile stress at 200 percent elongation, minimum, psi | 500 | 500 | 500 | 500 |
| Elongation at Rupture, minimum, percent | 300 | 300 | 300 | 300 |
| Set, maximum, percent | 30 | 20 | 30 | 30 |
| 2.AGING REQUIREMENTS (After air oven test at 100℃ +/- 1℃ for 168 hours) |  |  |  |  |
| Tensile strength, minimum, percentage of unaged value | 85 | 50 | 50 | 85 |
| Elongation at rupture, minimum, percentage of unaged value | 55 | 50 | 50 | 65 |
| 3.AGING REQUIREMENTS (After oil immersion test at 121℃+/-1℃ for 18 hours) |  |  |  |  |
| Tensile strength and elongation, minimum, percentage of unaged value | 60 | 60 | 60 | 60 |
| 4.ELECTRICAL REQUIREMENTS |  |  |  |  |
| Surface resistance,nonshielded cables minimum, megohms | 100 | 100 | 100 | 100 |

*Also known as Chlorosulfonyl Polyethylene

»  Table 5 Thermoplastic Jacket Requirements ........................................................

The jacket for mine power feeder cables shall be a crosslinked jacket meets the requirements of Table 4 or a thermoplastic jacket that meets the requirements of Table 5�

|  | Polyvinyl Chloride (PVC) | Chlorinated Thermoplastic Polyethylene (CM) | Thermoplastic Polyurethane (TPU) |
| --- | --- | --- | --- |
| 1.INITIAL PHYSICAL PROPERTIES |  |  |  |
| Tensile strength, minimum, psi | 1500 | 1400 | 3700 |
| Elongation at rupture, minimum, percent | 100 | 150 | 400 |
| 2.AIR OVEN AGING REQUIREMENTS |  |  |  |
| After conditioning@℃ +/- 1℃ | 100 | 121 | 100 |
| Hours | 120 | 168 | 168 |
| Tensile strength, minimum, percent of unaged value | 85 | 85 | 50 |
| Elongation, minimum, percent of unaged value | 60 | 50 | 75 |
| 3.OIL IMMERSION |  |  |  |
| After conditioning@℃ +/- 1℃ | 70 | 100 | 121 |
| Hours | 4 | 18 | 18 |
| Tensile strength, minimum, percent of unaged value | 80 | 60 | 60 |
| Elongation, minimum, percent of unaged value | 60 | 60 | 60 |
| 4.HEAT DISTORTION,121℃+/-1℃, maximum,percent | 50 | 25 | - |

»  Table 6 Heavy Duty Jackets Requirements (Type A) ............................................

The jacket for portable arc-welding cables shall be a heavy-duty jacket meets the requirements of Table 6 or a medium-duty jacket that meets the requirements of Table 7�

|  | Natural Rubber (NR) | Styrene Butadiene Rubber (SBR) | Neoprene (PCP) | Nitrile Butadiene (NBR)/ Polyvinyl Chloride (PVC)* | Chlorinated Polyethylene (CPE) ,Crosslinked | Ethylene Propylene Rubber (EPR) | Chloro- sulfonated Polyethylene (CSP/CSPE) |
| --- | --- | --- | --- | --- | --- | --- | --- |
| 1.PHYSICAL REQUIREMENTS |  |  |  |  |  |  |  |
| Tensile strength, minimum, psi | 3500 | 1800 | 1800 | 1800 | 1800 | 1800 | 1800 |
| Tensile strength, minimum, MPa | 24�1 | 12�4 | 12�4 | 12�4 | 12�4 | 12�4 | 12�4 |
| Tensile stress at 200 percent elongation, minimum, psi | 500 | - | 500 | 500 | 500 | 500 | 500 |
| Tensile stress at 200 percent elongation, minimum, MPa | 3�45 | - | 3�45 | 3�45 | 3�45 | 3�45 | 3�45 |
| Elongation at rupture, minimum, percent | 500 | 300 | 300 | 300 | 300 | 250 | 300 |
| Set, Maximum, percent | 15 | 20 | 20 | 30 | 30 | - | 30 |
| Tear, resistance, mimimum, pounds per inch | 40 | - | - | - | - | - | - |
| Tear, resistance, mimimum, kN/m | 7�01 | - | - | - | - | - | - |
| 2.AGING REQUIREMENTS |  |  |  |  |  |  |  |
| After air oven test at 100℃+/-1℃ for 168 hours |  |  |  |  |  |  |  |
| Tensile strength, minimum, percent of unaged value | - | - | 50 | 50 | 85 | 75 | 85 |
| Elongation at rupture, minimum percentage of unaged value | - | - | 50 | 50 | 55 | 75 | 65 |
| After air oven test at 70℃+/-1℃ for 168 hours |  |  |  |  |  |  |  |
| Tensile strength, minimum, psi | - | 1600 | - | - | - | - | - |
| Tensile strength, minimum, MPa | - | 11�0 | - | - | - | - | - |
| Elongation at rupture, minimum percentage | - | 250 | - | - | - | - | - |

|  | Natural Rubber (NR) | Styrene Butadiene Rubber (SBR) | Neoprene (PCP) | Nitrile Butadiene (NBR)/ Polyvinyl Chloride (PVC)* | Chlorinated Polyethylene (CPE) ,Crosslinked | Ethylene Propylene Rubber (EPR) | Chloro- sulfonated Polyethylene (CSP/CSPE) |
| --- | --- | --- | --- | --- | --- | --- | --- |
| After air pressure heat test at 127℃+/-1℃ for 20 hours |  |  |  |  |  |  |  |
| Tensile strength and Elongation at rupture, minimum, percent of unaged value | - | - | - | 50 | - | - | - |
| After oxygen pressure test at 70℃+/-1℃ for 96 hours |  |  |  |  |  |  |  |
| Tensile strength, minimum, psi | 2500 | 1600 | - | - | - | - | - |
| Tensile strength, minimum, MPa | 17�2 | 11�0 | - | - | - | - | - |
| Elongation at rupture, minimum percentage | 400 | 250 | - | - | - | - | - |
| After oxygen pressure test at 80℃+/-1℃ for 168 hours |  |  |  |  |  |  |  |
| Tensile strength and Elongation at rupture, minimum, percent of unaged value | - | - | - | 50 | - | - | - |
| After oil immersion test at 121℃+/-1℃ for 18 hours |  |  |  |  |  |  |  |
| Tensile strength and Elongation at rupture, minimum, percent of unaged value | - | - | 60 | 60 | 60 | - | 60 |

*Suitable for a minimum temperature of minus 10℃ (plus 14℉)

»  Table 7 Medium Duty Jackets Requirements (Type B).........................................

The jacket for portable arc-welding cables shall be a heavy-duty jacket meets the requirements of Table 6 or a medium-duty jacket that meets the requirements of Table 7�

|  | Styrene Butadiene Rubber (SBR) | Neoprene (PCP) | Nitrile Butadiene (NBR)/ Polyvinyl Chloride (PVC)* | Chlorinated Polyethylene (CPE) ,Crosslinked | Ethylene Propylene Rubber (EPR) | Chloro- sulfonated Polyethylene (CSP/CSPE) |
| --- | --- | --- | --- | --- | --- | --- |
| 1.PHYSICAL REQUIREMENTS |  |  |  |  |  |  |
| Tensile strength, minimum, psi | 1200 | 1200 | 1500 | 1500 | 1200 | 1200 |
| Tensile strength, minimum, MPa | 8�27 | 8�27 | 10�3 | 10�3 | 8�27 | 8�27 |
| Elongation at rupture, minimum, percent | 250 | 250 | 250 | 300 | 150 | 250 |
| Set, Maximum, percent | - | 20 | 30 | 35 | - | 30 |
| Tear, resistance, mimimum, pounds per inch |  |  |  |  |  |  |
| Tear, resistance, mimimum, kN/m |  |  |  |  |  |  |
| 2.AGING REQUIREMENTS |  |  |  |  |  |  |
| After air oven test at 100℃+/-1℃ for 168 hours |  |  |  |  |  |  |
| Tensile strength, minimum, percent of unaged value | - | 50 | 50 | 85 | 75 | 85 |
| Elongation at rupture, minimum percentage of unaged value | - | 50 | 50 | 55 | 75 | 65 |
| After oxygen pressure test at 70℃+/-1℃ for 48 hours |  |  |  |  |  |  |
| Tensile strength, minimum, psi | 1000 | - | - | - | - | - |
| Tensile strength, minimum, MPa | 6�89 | - | - | - | - | - |
| Elongation at rupture, minimum percentage | 100 | - | - | - | - | - |
| After oxygen pressure test at 80℃+/-1℃ for 168 hours |  |  |  |  |  |  |
| Tensile strength and Elongation at rupture, minimum percent of unaged value | - | - | 50 | - | - | - |

|  | Styrene Butadiene Rubber (SBR) | Neoprene (PCP) | Nitrile Butadiene (NBR)/ Polyvinyl Chloride (PVC)* | Chlorinated Polyethylene (CPE) ,Crosslinked | Ethylene Propylene Rubber (EPR) | Chloro- sulfonated Polyethylene (CSP/CSPE) |
| --- | --- | --- | --- | --- | --- | --- |
| After air pressure heat test at 127℃+/-1℃ for 20 hours |  |  |  |  |  |  |
| Tensile strength and Elongation at rupture, minimum, percent of unaged value | - | - | 50 | - | - | - |
| After oil immersion test at 121℃+/-1℃ for 18 hours |  |  |  |  |  |  |
| Tensile strength and Elongation at rupture, minimum percent of unaged value | - | 60 | 60 | 60 | - | 60 |

*Suitable for a minimum temperature of minus 10℃ (plus 14℉)