Caledonian Mining Cables

Portable Power Cables

Type W Four-Conductor Flat Portable Power Cable 2kV

» Applications .............................................................................................................

These flat parallel cables are designed for use on AC mining equipment, such as A�C� shuttle cars, drills, cutting and loading machines�

» Standards .................................................................................................................

ICEA S-75-381/NEMA WC 58 ASTM B 172

ASTM B 33

CAN/CSA C22�2 No� 96

» Construction ............................................................................................................

Stranded Tinned Copper Conductor

EPR Insulation

Synthetic Yarn Braid Renforcement

Conductors:

Stranded annealed tinned copper conductor�

Insulation:

Ethylene Propylene Rubber (EPR)�

Reinforcement: Synthetic yarn� Jacket:

CPE Jacket

Heavy-duty/extra-heavy-duty Chlorinated Polyethylene (CPE), black� (Cables having a nominal outside diameter of more than 2�0 inches require extra-heavy-duty jackets�)

» Options .....................................................................................................................

- Other jacket materials such as CSP/PCP/NBR/PVC are available upon request�

- Two-layer jacket with reinforcing fibre between the two layers can be oﬀered  as an option�

www.caledonian-cables.co.uk  www.addison-cables.com	9

Caledonian Mining Cables

Portable Power Cables

»  Mechanical and Thermal Properties ......................................................................

Minimum Bending Radius: 6×OD

Maximum Conductor Operating Temperature: +90℃

»  Dimensions and Weight ..........................................................................................

| Construction | No. of Strands | Nominal Insulation Thickness |  | Nominal Jacket Thickness |  | Nominal Overall Diameter Height×Width |  | Nominal Weight |  | Ampacity |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
| No. of cores×AWG/kcmil | - | inch | mm | inch | mm | inch | mm | lbs/kft | kg/km | A |
| 4×6 | 133 | 0�06 | 1�5 | 0�095 | 2�4 | 0�67×1�69 | 17�0×42�9 | 895 | 1332 | 72 |
| 4×4 | 259 | 0�06 | 1�5 | 0�110 | 2�8 | 0�75×1�89 | 19�0×48�0 | 1185 | 1764 | 93 |
| 4×2 | 259 | 0�06 | 1�5 | 0�110 | 2�8 | 0�84×2�23 | 20�6×56�6 | 1620 | 2411 | 122 |
| 4×1 | 259 | 0�08 | 2�0 | 0�125 | 3�2 | 0�97×2�60 | 24�6×66�0 | 2100 | 3125 | 143 |
| 4×1/0 | 259 | 0�08 | 2�0 | 0�140 | 3�6 | 1�01×2�73 | 25�7×69�3 | 2500 | 3721 | 165 |
| 4×2/0 | 329 | 0�08 | 2�0 | 0�140 | 3�6 | 1�10×2�96 | 27�9×75�2 | 2900 | 4316 | 192 |
| 4×3/0 | 413 | 0�08 | 2�0 | 0�155 | 3�9 | 1�18×3�25 | 30�0×82�6 | 3500 | 5209 | 221 |
| 4×4/0 | 532 | 0�08 | 2�0 | 0�155 | 3�9 | 1�29×3�46 | 32�8×87�9 | 4225 | 6288 | 255 |

Ampacity-Based on a conductor temperature of 90℃ and an ambient air temperature of 40℃, per ICEA S-75-381�

10	www.caledonian-cables.co.uk  www.addison-cables.com