Caledonian Mining Cables

Portable Power Cables

Type G Two-Conductor Round Portable Power Cable 2kV

» Applications .............................................................................................................

These cables are designed for use in heavy duty services as power supply cable, mobile and portable electrical�

» Standards .................................................................................................................

ICEA S-75-381/NEMA WC 58 ASTM B 172

ASTM B 33

CAN/CSA C22�2 No� 96

» Construction ............................................................................................................

Stranded Tinned Copper Conductor EPR Insulation

Grounding Conductor Reinforced CPE Jacket

Conductors:

Stranded annealed tinned copper conductor�

Insulation:

Ethylene Propylene Rubber (EPR)�

Grounding Conductor:

Tinned copper conductor with an optional green outer covering�

Jacket:

Reinforced heavy-duty/extra-heavy-duty Chlorinated Polyethylene (CPE), black� (Cables having a nominal outside diameter of more than 2�0 inches require extra-heavy-duty jackets�)

www.caledonian-cables.co.uk  www.addison-cables.com	17

Caledonian Mining Cables

Portable Power Cables

» Options .....................................................................................................................

- Other jacket materials such as CSP/PCP/NBR/PVC are available upon request�

- Two-layer jacket with reinforcing fibre between the two layers can be oﬀered  as an option�

»  Mechanical and Thermal Properties ......................................................................

Minimum Bending Radius: 6×OD

Maximum Conductor Operating Temperature: +90℃

»  Dimensions and Weight ..........................................................................................

| Construction | No. of Strands | Grounding Conductor Size | Nominal Insulation Thickness |  | Nominal Jacket Thickness |  | Nominal Overall Diameter |  | Nominal Weight |  | Ampacity |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
| No. of cores×AWG/ kcmil | - | AWG/ kcmil | inch | mm | inch | mm | inch | mm | lbs/kft | kg/km | A |
| 2×8 | 133 | 10 | 0�06 | 1�5 | 0�110 | 2�8 | 0�81 | 20�6 | 495 | 736 | 72 |
| 2×6 | 259 | 10 | 0�06 | 1�5 | 0�125 | 3�2 | 0�93 | 23�6 | 650 | 967 | 95 |
| 2×4 | 259 | 8 | 0�06 | 1�5 | 0�140 | 3�6 | 1�08 | 27�4 | 940 | 1399 | 127 |
| 2×2 | 259 | 6 | 0�06 | 1�5 | 0�155 | 3�9 | 1�27 | 32�3 | 1360 | 2023 | 167 |
| 2×1 | 259 | 5 | 0�08 | 2�0 | 0�170 | 4�3 | 1�44 | 36�6 | 1730 | 2574 | 191 |
| 2×1/0 | 259 | 4 | 0�08 | 2�0 | 0�170 | 4�3 | 1�52 | 38�6 | 2000 | 2976 | 217 |
| 2×2/0 | 259 | 3 | 0�08 | 2�0 | 0�170 | 4�3 | 1�65 | 41�9 | 2240 | 3333 | 250 |
| 2×3/0 | 259 | 2 | 0�08 | 2�0 | 0�190 | 4�8 | 1�77 | 45�0 | 2860 | 4255 | 286 |
| 2×4/0 | 259 | 1 | 0�08 | 2�0 | 0�190 | 4�8 | 1�92 | 48�8 | 3500 | 5207 | 328 |

Ampacity-Based on a conductor temperature of 90℃ and an ambient air temperature of 40℃, per ICEA S-75-381�

18	www.caledonian-cables.co.uk  www.addison-cables.com