Caledonian Mining Cables Cables for Underground Mining

(N)TSCGECWOEU Medium Voltage Trailing Cable

»  Applications

These cables are used for the connection of electrical equipment, in mines and underground excavations with hazardous environments under particularly high mechanical loads, e.g. high-voltage transformers on power lines in underground mining and tunnelling.

»  Standards

Based on VDE 0250 Part 813

»  Construction

Stranded Copper Conductor 3GI3 Rubber Insulation Optional Pilot Cores

Earth Conductor GM1b Inner Sheath Monitoring Conductor

5GM5 Rubber Outer Sheath

Conductors: Flexible stranded copper conductor, class 5 according to DIN VDE 0295.

Inner Conductor Layer: Special rubber compound, conductive.

Insulation: Rubber type 3GI3.

Outer Conductor Layer: Special rubber compound, conductive, easy strippable.

Pilot Cores (optional): Tinned copper conductor with EPR insulation.

Earth Conductor: Spiral of tinned copper wires.

Inner Sheath: Rubber type GM1b.

Monitoring Shield/Armour: Braided armour of combined copper-steel wires; or wrap of copper and steel wires, copper tape in opposite direction, reinforcing tape.

Outer Sheath: Rubber type 5GM5.

www.caledonian-cables.co.uk  www.addison-cables.com	33

Caledonian Mining Cables

Cables for Underground Mining

»  Dimensions and Weight

6/10kV

| Number of Cores×Nominal Cross Section | Minimium Overall Diameter | Maximum Overall Diameter | Nominal Weight |
| --- | --- | --- | --- |
| No. ×mm² | mm | mm | kg/km |
| 3×25+3×16/3E+3×2�5ST+6UEL | 48�0 | 52�0 | 3500 |
| 3×35+3×16/3E+3×2�5ST+6UEL | 51�0 | 55�0 | 3750 |
| 3×50+3×25/3E+3×2�5ST+6UEL | 56�0 | 60�0 | 4720 |
| 3×95+3×50/3E+3×2�5ST+6UEL | 66�0 | 71�0 | 7260 |
| 3×120+3×70/3E+6UEL | 70�0 | 75�0 | 9700 |
| 3×150+3×70/3E+6UEL | 73�0 | 78�0 | 9950 |

12/20 (24) kV

| Number of Cores×Nominal Cross Section | Minimium Overall Diameter | Maximum Overall Diameter | Nominal Weight |
| --- | --- | --- | --- |
| No. ×mm² | mm | mm | kg/km |
| 3×25+3×25/3E+6UEL | 62�0 | 67�0 | 5800 |
| 3×95+3×50/3E+6UEL | 74�0 | 78�0 | 11000 |
| 3×120+3×70/3E+6UEL | 80�0 | 85�0 | 13000 |

34	www.caledonian-cables.co.uk  www.addison-cables.com