Caledonian Mining Cables Cables for Open-cast Mining

(N)TSCGEWOEU Medium Voltage Reeling Cable With Fiber Optics

»  Applications

These cables are used for connection of large mobile equipment such as excavators and spreaders, gantry cranes, etc., under very high mechanical loads, suitable for motorised reeling on monospiral or level-wind reelers.

»  Standards

Based on VDE 0250 Part 813

»  Construction

3GI3 Rubber Insulation Stranded Copper Conductor Fibre Optic Element

GM1b/5GM3 Rubber Inner Sheath Polyester Braid

Earth Conductor

5GM3/5GM5 Rubber Outer Sheath

Conductors: Flexible stranded copper conductor, class 5 according to DIN VDE 0295.

Inner Conductor Layer: Semiconductive layer.

Insulation: EPR type 3GI3.

Outer Conductor Layer: Semiconductive layer.

Earth Conductor: Split into two in the outer interstices.

Inner Sheath: Rubber type GM1b/5GM3.

Fiber Optics: 12 FO 50/125 or 62.5/125 or E9/125μm within protection sheath.

Reinforcement: Polyester anti-torsion braid.

Outer Sheath: Rubber type 5GM3/5GM5, flame retardant and oil resistant.

www.caledonian-cables.co.uk  www.addison-cables.com	47

Caledonian Mining Cables

Cables for Open-cast Mining

»  Dimensions and Weight

3.6/6 kV

| Number of Cores×Nominal Cross Section | Minimium Overall Diameter | Maximum Overall Diameter | Nominal Weight |
| --- | --- | --- | --- |
| No. ×mm² | mm | mm | kg/km |
| 3×25+2×25/2+12×LWL | 39�0 | 42�0 | 2410 |
| 3×35+2×25/2+12×LWL | 42�0 | 45�0 | 2995 |
| 3×50+2×25/2+12×LWL | 45�0 | 48�0 | 3645 |
| 3×70+2×35/2+12×LWL | 50�0 | 54�0 | 4760 |
| 3×95+2×50/2+12×LWL | 54�0 | 58�0 | 5580 |
| 3×120+2×70/2+12×LWL | 58�0 | 62�0 | 6690 |
| 3×150+2×70/2+12×LWL | 63�0 | 67�0 | 7990 |
| 3×185+2×95/2+12×LWL | 67�0 | 72�0 | 9330 |

6/10 kV

| Number of Cores×Nominal Cross Section | Minimium Overall Diameter | Maximum Overall Diameter | Nominal Weight |
| --- | --- | --- | --- |
| No. ×mm² | mm | mm | kg/km |
| 3×25+2×25/2+12×LWL | 40�0 | 43�0 | 2450 |
| 3×35+2×25/2+12×LWL | 43�0 | 46�0 | 3035 |
| 3×50+2×25/2+12×LWL | 46�0 | 49�0 | 3690 |
| 3×70+2×35/2+12×LWL | 51�0 | 55�0 | 4800 |
| 3×95+2×50/2+12×LWL | 55�0 | 59�0 | 5620 |
| 3×120+2×70/2+12×LWL | 59�0 | 63�0 | 6740 |
| 3×150+2×70/2+12×LWL | 64�0 | 68�0 | 8040 |
| 3×185+2×95/2+12×LWL | 68�0 | 72�0 | 9380 |

12/20 kV

| Number of Cores×Nominal Cross Section | Minimium Overall Diameter | Maximum Overall Diameter | Nominal Weight |
| --- | --- | --- | --- |
| No. ×mm² | mm | mm | kg/km |
| 3×25+2×25/2+12×LWL | 46�0 | 49�0 | 3050 |
| 3×35+2×25/2+12×LWL | 49�0 | 52�0 | 3490 |
| 3×50+2×25/2+12×LWL | 53�0 | 57�0 | 4340 |
| 3×70+2×35/2+12×LWL | 57�0 | 61�0 | 5320 |
| 3×95+2×50/2+12×LWL | 61�0 | 65�0 | 6360 |
| 3×120+2×70/2+12×LWL | 67�0 | 71�0 | 7810 |
| 3×150+2×70/2+12×LWL | 70�0 | 74�0 | 8900 |
| 3×185+2×95/2+12×LWL | 76�0 | 80�0 | 10700 |

48	www.caledonian-cables.co.uk  www.addison-cables.com

Caledonian Mining Cables Cables for Open-cast Mining

18/30 kV

| Number of Cores×Nominal Cross Section | Minimium Overall Diameter | Maximum Overall Diameter | Nominal Weight |
| --- | --- | --- | --- |
| No. ×mm² | mm | mm | kg/km |
| 3×25+2×25/2+12×LWL | 55�0 | 59�0 | 3960 |
| 3×35+2×25/2+12×LWL | 58�0 | 62�0 | 4550 |
| 3×50+2×25/2+12×LWL | 63�0 | 67�0 | 5510 |
| 3×70+2×35/2+12×LWL | 66�0 | 70�0 | 6560 |
| 3×95+2×50/2+12×LWL | 71�0 | 75�0 | 7850 |
| 3×120+2×70/2+12×LWL | 76�0 | 80�0 | 10690 |
| 3×185+2×95/2+12×LWL | 86�0 | 90�0 | 12550 |

www.caledonian-cables.co.uk  www.addison-cables.com	49